Austin Public Library

Austin History Center

Disaster Preparedness Plan

Revision of plan prepared by

Jean Jones Kile and

Rebecca Rich-Wulfmeyer

Subsequent revisions prepared by Cynthia Lewis

with the assistance of the staff of the Austin History Center

Special thanks to Erin Norris, Reference Librarian I

Austin Public Library-Austin History Center

January 2007

Table of Contents

Acknowledgments/Credits	8

Introduction	8

Purpose and Scope	8

Distribution	8

Disaster Team Members	8

The Recovery Team	 10

Priorities	10

General Tips for the Safety of People and Collections	12

Staff Evacuation Procedures	12

Recovery	12

Collection Recovery Priorities	14

Emergency Resources	14

Emergency Equipment and Supplies	14

Fire alarm pulls	14

Fire extinguishers	15

First Aid kits	15

Infection Control Kits	15

Sprinkler System	15

Transistor radio (battery powered)	15

Weather Radio	16

Emergency Services	16

Ambulance	16

Carpenters	16

Chemist	16

Data processing backup	16

Electrician	16

Emergency management coordinator	16

Exterminator	16

Fire department	16

Food services	17

Locksmith	17

Micrographics vendor—handles all Austin American Statesman Microfilm	17

Plumber	17

Police department	17

Preservation Services	17

Security personnel (extra)	18

Software vendor	18

Temporary personnel	18

Utility companies:	18

Electric	18

Gas	18

Disaster Recovery Resources	19

Disaster Recovery Supplies	19

Disaster Preparedness Kit	19

Bone folders	19

Book Trucks	20

Boxes/Milk Crates	20

Brushes	20

Bubble wrap	20

Buckets, plastic garbage cans, trash can liners, rubber gloves, garden hose	20

Camera and film	21

Cellular Phones	21

Chemical Sponge	21

Dehumidifiers	21

Dish pans, plastic	21

Distilled water	21

Dollies	21

Dry Ice	21

Drying Space	21

Dust Masks	21

Extension cords	21

Fans (including Shop Fans)	22

Flashlight batteries and bulbs	22

Fork Lift	22

Freezer Paper	22

Freezer space	22

Fungicides	22

Garden hose	22

Generators and Lights (Portable)	22

Hand trucks	22

Hard hats	22

Hardware Stores	22

Hygrothermograph	23

Kodak Photoflo	23

Ladders	23

Mops, sponges, buckets, cleaning supplies and brooms	23

Pallets	23

Paper towels (not colored)	23

Plastic Bags	23

Plastic Sheeting	23

Polyester film (preferably 3 mil)	23

Polyester web	24

Pumps (submersion)	24

Ramps	24

Rental Companies	24

Refrigeration truck	24

High-efficiency particulate air (HEPA) Respirators	24

Rubber boots or overshoes	24

Safety glasses	24

Scaffolding	24

Shovels	24

Spotlights	24

Trash cans (plastic, small and large)	24

Unprinted Newsprint	24

Vacuum/freeze drying facilities	25

Walkie talkies	25

Water, drinking	25

Waterproof clothing	25

Wax crayon	25

Weights	25

Wet/dry vacuum	25

Wheelbarrows	25

Wood, lumber	25

Worktable and chairs	26

Disaster Recovery Services and Conservation Contacts	26

AMIGOS Preservation Service	Error! Bookmark not defined.

Blackmon-Mooring Steamatic Catastrophe, Inc.	26

Belfor, U.S.A.	27

SOLEX Environmental Systems	27

Harry Ransom-Humanities Research Center	27

Library of Congress, National Preservation Program Office, Preservation Directorate	27

Northeast Document Conservation Center	27

Eastman Kodak	28

Southwest Micropublishing, Inc.	28

Photographic Processing	28

Photo Supplies	28

American Institute for the Conservation of Historic and Artistic Works (FAIC)	28

Computer data and hardware recovery	29

Federal Emergency Management Agency	29

Local Contacts	29

Fire	29

Prevention Activities	29

Emergency Procedures	30

Basic Fire Procedures	30

When You See a Fire	31

When You Hear the Fire Alarm	31

For Evacuation	32

Recovery Procedures	33

FIRE DAMAGED MATERIALS	33

Access	34

For Further Reading	35

Water	36

Prevention Activities	36

Emergency Procedures	36

Recovery Procedures	37

Cleaning And Drying	37

Air Drying	38

How Water Affects Books And Unbound Materials	44

Estimating Water Absorption	44

Access	46

Stabilizing the Environment	46

Assessment Of Damage And Planning For Salvage	47

Primary Considerations For Recovery Of Water-Damaged Collections	48

Preliminary Steps In The Evacuation From Water-Damaged Areas	48

Removal And Packing Of Water-Damaged Materials -- The Work Force	49

Removal From Water-Damaged Area -- The Catalog And Other Records Of the Collection	49

Removal and Packing	50

Disposition of Remaining Materials and Cleaning of Water Exposed Areas	51

Cleaning After a River Flood	51

Thorough Washing to Remove Heavy Deposits of Mud	52

Principles of Stabilization by Freezing	52

Cold Temperature Storage Conditions	53

Evaluation of Loss	59

Summary of Emergency Procedures	60

For Further Reading	61

Water Damage Recovery Procedures Chart	62

Infestation	65

Prevention Activities	65

Emergency Procedures	65

Recovery Procedures	65

Short Term Response Actions	65

Long Term Recovery Actions	66

For Further Reading	66

Mold and Other Growths	68

Prevention Activities	68

Prevention	68

The Microorganisms	68

Susceptible Materials	69

Damage	69

Emergency Procedures	69

Detection	70

Recovery Procedures	70

More on Mold	71

Treatment	72

For Further Reading	73

Collapse of Shelving and Other Indoor Structural Accidents	74

Theft and Vandalism	75

Prevention Activities	75

Theft	75

Vandalism	75

Reading Room Security	76

Emergency Procedures	77

Recovery Procedures	77

For Further Reading	78

Data Loss	78

Prevention Activities	78

Recovery Procedures	78

For Further Reading	79

Hazardous Materials and Fumes	80

Chemical Spills	82

Prevention Activities	82

Emergency Procedures	82

Recovery Procedures	82

Terrorism	83

Emergency Procedures	83

Terrorism in General	83

Bomb Threat	83

Nuclear, Biological and Chemical Weapons	88

Explosion	91

Emergency Procedure	91

Recovery Procedures	91

Immediate Actions	92

Short Term Response and Long Term Recovery Actions	92

Severe Storms	93

Prevention Activities	93

Weather Definitions	93

Emergency Procedures	96

Storm Watch	96

Storm Warning	96

Tornado	97

Winter Storm	97

Recovery Procedures	98

For Further Reading	99

Major Traffic Accident	99

Bibliography	100

Planning for Disaster

Building Survey

Risk Assessment Form:  Fire

Risk Assessment Form:  Water

Risk Assessment Form:  Security

Risk Assessment Form: Interior Risks

Risk Assessment Form: Exterior Risks

Information Update Form

Acknowledgments/Credits

From the National Park Service. Disaster Plan. [Web page]:

http://www.cr.nps.gov/museum/publications/primer/primintro.html [Accessed December 16, 2003].

Introduction

Purpose and Scope

The purpose of this disaster preparedness plan is to reduce the risk of material loss to the Austin History and Records Center collections.  This plan covers fire, water, infestation and mold, theft and vandalism, data loss, chemical spills, bomb threats, and tornadoes as potentially disastrous events.  The plan addresses issues of prevention, emergency action, and recovery in the event of any of the above disasters.

Distribution

Disaster Team Members with an asterisk (*) by their names have copies of this plan.  Also, individuals in the following positions have copies of this plan.

*	APL Director (Brenda Branch)

*	All APL Security officers (Security Supervisor)

*	Any other agencies that occupy the building

*	Fire Department Battalion Captain

*	Emergency Management

An additional copy of the plan is available for the entire AHC staff in two locations:  Staff Reference Shelf (by the floor safe in the General Collection area) and at the Reading Room I desk by the cash register.  There are also copies of the Disaster Preparedness Plan in the Disaster Kits in the AHC ground floor supply room and in the AHC area of the Central basement

Disaster Team Members

*Leader:  Susan K. Soy, AHC Manager

Phone Contact Information: Work:(512) 974-7388

Email:  sue.soy@ci.austin.tx.us and ssoy@ischool.utexas.edu

*Leader:  John Gillum, Facilities Planning Manager

Phone Contact Information:  (512) 974-7495

Email:  john.gillum@ci.austin.tx.us

*Member:  Michael Miller, Assistant AHC Manager

Phone Contact Information:  Work (512) 974-7436

Email: mike.miller@ci.austin.tx.us

*Leader: Toni Lambert, Asst. Director of Public Services, ACAO

Phone Contact Information: (512) 974-7466

Email:  toni.lambert@ci.austin.tx.us

*Alternate: Public Services Librarian

Phone Contact Information:  (512) 974-7392

Email:  ________________________

*Member: Ben Grillot, Photographs Curator

Phone Contact Information:Work:(512) 974-7386

Email:  ben.grillot@ci.austin.tx.us

*Alternate:  Ruth Baker, Processing Archivist

Phone Contact Information: Work: (512) 974-7382

Email:  ruth.baker@ci.austin.tx.us

*Records Manager:  Jannette Goodall, City Records Manager

Phone Contact Information:  974-9045

Email: jannette.goodall@ci.austin.tx.us

*Building Facilities Services:  Armando Cubriel, Building Services Asst. Manager

Phone Contact Information:  (512) 974-7494

Email: Mando.Cubriel@ci.austin.tx.us

*Building Facilities Services:  Floyd Hodges, General Maintenance Supervisor

Phone Contact Information:  (512) 974-7496

Email: Ramon.Cantu@ci.austin.tx.us

*Building Security:  Val Musson, Security Supervisor

Phone Contact Information:  (512) 974-7412 Pager: (512)802-7022

Email: Val.Musson@ci.austin.tx.us

Legal Advisor:  Eyna Canales- Zarate, Asst. Director of Adm.& Support Services

Phone Contact Information:  (512) 974-7446

Email: Eyna.Canales@ci.austin.tx.us

AHC Personnel with Work Extension Telephone Numbers (This list will be updated annually – for the most up-to-date list, see the personnel telephone tree list given to each AHC staff member.)

| Baker, Ruth | 47382 | Lilly, Sharmyn-AHCA | 47499 |
| --- | --- | --- | --- |
| Gonzales, Irene | 47389 | McEvoy, Grace | 47396 |
| Hamblin, Tim | 47305 | Wyckoff, Karen | 47580 |
| Holmes, Pegy | 47580 | Riles, Karen | 47390 |
| Jordan, Scott | 47580 | AHCA Secretary | 47383 |
| vacant | 47392 | Grillot, Ben | 47386 |
| Soy, Susan | 47388 | Murphy, Rita | 47580 |
| Miller, Mike | 47436 |  |  |

Walkie-talkie By Copier:  Unit  3  (checked regularly by APL Security Staff)                       APL Security Pager 802-7022

The Recovery Team

Conducting a successful and efficient recovery operation after a major flood or similar disaster requires, in addition to a good supply of dedicated labor, a team of experts who should be assembled before practical work begins.

The leader should be a person who has had practical experience and understands the effects of different environmental conditions on water-soaked materials of all types, conditions, and ages. The team leader should be assisted by custodians who know the collection intimately; conservators who can provide additional advice and guidance as well as help in training workers in safe removal procedures. Procurement specialists, building maintenance engineers, electricians, carpenters, plumbers, a chemist if available, health and safety experts, are all part of the recovery team.

One person or more who is familiar with national and local resources is highly desirable to assist in locating and procuring the special facilities, equipment and supplies needed during the operation. They should be familiar with using the Yellow Pages to track down materials and equipment, be able to seek out the key chemical supply companies in the country and generally have the authority to cut through administrative red tape.

The assembled team should be carefully briefed on the recovery plan and procedures to be followed as well as various contingency alternatives which might have to be adopted, priorities to be observed, and their own specific responsibilities.

Team leaders need to be identified and instructed in the details of the recovery plan and its main aims and goals. They in turn should brief all workers so that they too will understand the purpose of the plan and what is expected of each of them. A well briefed and dedicated team works much better than enthusiastic individuals who are allowed to carry out actions which may be disruptive to the main purpose of the team plan.

The major objectives of this team should be:

·	To stabilize the condition of the materials before removal by creating the environment necessary to prevent further damage.

·	To recover the maximum number of material from the damaged collections in a manner that will minimize the need for future restoration and its costs. From National Park Service. Disaster Plan. [Web page]. http://www.cr.nps.gov/museum/publications/primer/primintro.html [Accessed December 16, 2003]

Priorities

Although this disaster preparedness plan emphasizes the protection of the collections, human safety is always paramount.  The following priorities are recognized as governing the general framework of decision-making in the event of an emergency in the Austin History Center.

*	Priority 1	Human safety including the evacuation of buildings

*	Priority 2	Collections and essential records protection and recovery.  		Refer to collection priority maps located at the back of the manual.

*	Priority 3	Electronic equipment protection and recovery

*	Priority 4	Fittings and furniture protection and recovery

General Tips for the Safety of People and Collections

1.   Maintain constant temperature and humidity.

2.   Follow closing procedures nightly.

3.   Keep up with housekeeping basics.

4.   Check for problems annually.

5.   Know where the fire extinguishers are located.

6.   Know where the emergency exits are located.

7.   Know where the severe weather stations are located.

8.   Keep the sign-in board up to date as to your whereabouts at all times.

9.   Make sure your volunteers use the sign-in board at all times.

10. Familiarize staff with plan and use safety drills to reinforce.

Staff Evacuation Procedures

When evacuation alarm sounds or you are directed to evacuate the facility:

1.	Remain calm.

2.	Shut down all hazardous operations.

3.	Follow instructions.

4.	Assist disabled persons.

5.	Leave the area in an orderly fashion.  Close doors, but do not lock.

6.	Follow established evacuation routes.

7.	Move away from the structure.  Go directly to the assembly area.  Report to the Evacuation Coordinator for a "head count".

8.	Do not block the street or driveway.

9.	Stay at the assembly area until instructed otherwise. Ibid.

Recovery

The Library is a member of AMIGOS and the AMIGOS Preservation & Recovery Service is available to consult before, during, and after the disaster.

AMIGOS Preservation Service

14400 Midway Road

Dallas, TX 75244-3509

(800) 843-8482; (972) 851-8000; Fax (972) 991-6061

Daytime procedure: Call main Amigos number and ask for: Elizabeth Klein, ext. 2844 email: klein@amigos.org.  If she cannot help, she will route the call to someone who can.  Always call the main number first in case she is out of the office.  If Elizabeth is out, ask for Gina Minks (2825) IPS Management, Bill Walker (2853) for Imaging Field Services.  Rebecca Elder is the Adjunct Preservation Field Services Officer. Amigos Support Desk (2863). The after hours emergency number is Elizabeth Klein’s cell phone: 1-469-223-4900. After hours calls may be routed to other staff for additional assistance. Any time there is a problem reaching someone during the day by calling the Amigos main number, call Elizabeth’s cell phone.

Before recovery steps can be taken, the facility must be declared safe to enter by professionals such as the fire marshal or the police department.  While waiting for the facility to be declared safe, staff should do the following:

1.	Gather supplies.  (See supplies in Resources sections.)

2.	Establish a work site and transport supplies there.  This area should be designated in advance, and should be appropriate to the task at hand (large enough for full-scale restoration, able to be climate-controlled, etc.)

3.	Contact Disaster Recovery Services, such as AMIGOS, listed in the Resources sections.

Once it is safe to enter the building, the following steps should be taken:

1.	Assess the damage. Consult conservators and disaster professionals.  Alert them to your priorities (these are marked on the Priority Maps at the back of this plan.)  Original documents, photographs, and negatives take first priority.

2.	Lower the temperature and relative humidity.  Open windows and doors, turn on the air conditioning, and use fans to circulate hot, humid air out of the building.  Mold infestation can occur very rapidly in hot, humid conditions; wet materials are extremely susceptible to mold.

3.	Gather experts and conduct a detailed walk-through of the collection.  If the majority of damage is due to water, take notes on the approximate length of time materials have been wet and the temperature of the water. This information will help the conservator in treating materials.

4.	Document damage.  Retrieve the camera from the Photo Collection Room and photograph the area.  Take as extensive notes as time permits -- these will be necessary when filing insurance claims, as well as aiding in relocating materials after restoration.

5.	Take advice from the experts and work quickly.  Alert them to your collection priorities and allow them to instruct you in the most appropriate salvage methods. Conservators or disaster response professionals can help you determine which of your materials can be saved.

6.	Gather disaster team and assign duties (see Disaster Team Members in Contacts section).  Arrange for transport of materials to the salvage site.  Decide on which salvage techniques will be used, and set up an assembly line.  Bring in outside assistance, if necessary.  (See Local Contacts section).  Some damp materials may be air-dried, but any valuable materials that have been soaked should probably be frozen immediately to prevent further deterioration.  Some old photographs should not be frozen.  For a list of salvage techniques by item, see Water Damage Recovery Procedures Chart in the Water section.  Never begin major restoration activities on valuable materials before consulting professionals.

7.	Call Disaster Recovery Assistance Services.  (See list in Resources sections for appropriate ones to type of disaster.)   Bring in experts for all salvage of valuable materials.  Eastman Kodak will provide advice on treatment of fire or water damaged film.

8.	The Austin History Center is “self-insured” by the City of Austin.  Immediately contact City Officer, Emergency Management, William S. Collier 974-0461 about insurance claims.

Collection Recovery Priorities

Archives:

First Floor:  First two ranges of boxes in archival stacks area.  Archival collections inventories are on the shelf against south wall of Archives Room.  Donor file cabinets are on the left upon entering the room from the first floor hallway.  O. Henry Collection in O. Henry Room on east end of hallway on the south side of the hallway.

Second Floor:  Police ledgers in oversized archives (ground floor).

Architectural Archives:

Ground Floor Architectural Archives:  Travis County Courthouse drawings and Austin History Center drawings, both in Cabinet #7, bottom two drawers.

General Collection:

Ground Floor: Travis County School Records, with other Travis County Records in Archives Stacks, west wall.

First Floor: General Collection: City Directories are in the Reading Room on the north wall.

Periodicals Collection:

First Floor:  Newspaper Index Card Files 1878-1883 and 1956-1973, to the left of the door to the Photo Collection Room.

Photography Collection:

Ground floor:  Photography Lab -- Austin File Negatives are on the counter beneath window, on the counter against the east wall of workroom, and in the file cabinet in the alcove at the front door.

First floor:  Photographs in file cabinets along the north and west walls of Photo Collection Room.

Emergency Resources

Emergency Equipment and Supplies

Fire alarm pulls:

Fire alarm pulls can be found in the following locations:

Ground Floor: 1)Architectural Drawings Room, to the right of the exit door; 2)The Exhibits Area, by the exit door on the west wall (near Art Rack Room); 3)Art Rack Room, to the right of the south exit door; 4) On the wall to the right when entering the south employee entrance.

First floor: 1) Lobby, outside the Reception Room kitchen door; 2) Hallway leading to Guadalupe Street exit, to the right of the O. Henry Room doors.

Second floor: 1) Landing of stairs leading to staff offices, nearest Room 203

Outer vault: 1) On stairwell wall, east side of room – when coming from the elevator into outer vault, it is on the wall facing you, to the right of the oversize photograph boxes

Fire extinguishers

Fire extinguishers are located throughout the building. See Evacuation Diagrams, pp. 32-34 for locations of fire extinguishers.

Ground Floor:  1) Art Rack Room 2) Exhibit Specialist’s Office (inside entrance from the kitchen) 3) Hallway (next to water fountain near kitchen) 4) Architecture Archives (on column in middle of room) 5) Closet behind elevator (next to Ladies Restroom) 6) Travis County Records, 7) Hallway leading to parking lot (next to Photo Lab entrance) 8) Photo Lab (inside entrance) 9) Photo Lab (Printing Room) 10) Photo Lab (Hallway near stairs), 11) Video area (by steps leading to raised office area in northeast work room), 12) Video area (inside entrance to the southeast work room.

First Floor:  1) Reading Room (next to swinging door) 2) Staff Work Area (inside, by swinging door) 3) Microfilm Room 4)Photo Room 5) Stacks (on north wall) 6) Archivist Office (inside entrance) 7) Kitchen 8) Reception Room (east side of fire place) 9) Archives Room (inside entrance) 10) Across from Elevator 11) Stairwell leading down to Architectural Archives          12) Mayor’s Room (on floor, to right when entering).

Second Floor:  1) Archives Balcony (on left as you exit to stacks) 2) Stacks (on north wall)             3) Staff Office Area (to right of entrance to Public Service Librarian’s office).

Third Floor:  1) Inner Vault (on left as you enter) 2) Outer Vault (by door leading to stairwell).

First Aid kits-updated by AHC safety officer February, 2007

First Aid Kits are located on all floors.

Ground Floor:  Top of the Staff Room refrigerator, Exhibits area on shelf as you enter from staff room, Video area on the shelf - west wall of the office area, Photo Lab – cabinet under the negatives on the south wall, Hallway – open shelf where Waterloo press is stored.

First Floor:  Bottom right drawers of RR1 & RR2.  Staff Reference shelf. Archives Room on the shelves next to Archives Curator’s desk. Kitchen – on top of the refrigerator.

Second Floor:  Top of the file cabinet next to Public Services Librarian’s office.

Infection Control Kits-updated by AHC safety officer February, 2007

Infection Control Kits provide a gown, gloves, mask, protective glasses, shoe covers, waste scoops and antimicrobial wipes to use in situations where cross-contamination by blood-borne and saliva-borne diseases is possible.

Ground Floor: Top of Staff Room refrigerator

First Floor:  Reading Room, in RRI bottom right drawer, Reading Room stacks –near vol. mailboxes, top of the Reception Room kitchen refrigerator.

Second Floor:  Top of wooden filing cabinet next to Public Services Librarian’s office.

Sprinkler System

Activated only in the vault area of the History Center.

Transistor radio (battery powered)

Photo Lab, next to enlarger in printing room.  Batteries are in drawer under radio. Regularly checked by security staff.

Weather Radio

Located in the General Collection area on top of the safe.  This radio is equipped with a 9-volt battery back up which is changed every six months by the Library Security Staff.  Staff should take Weather Radio with them when they take cover in protected areas during severe weather.

Emergency Services

The following list is of emergency services that should be contacted (if needed) in the event of a disaster.

Ambulance

Use 911 and then notify Security at 802-7022; Use radio units if necessary.

Carpenters

Facilities Services will select carpenters

Chemist

Karen Pavelka, UT HRC, will be consulted concerning chemists

Contact information: pavelka@mail.utexas.edu or (512) 471-8286

Data processing backup

The Library Server’s Libnwfs01 (File/Print Server) and Libnt01 (Primary Domain Controller) are both on a 3 week rotation, doing a full backup each day.  One set of Disaster Recovery tapes is kept at JHF and the other at AHC.

Jim Greco

974-7454 phone

802-7038 pager

974-7578 fax

Electrician

Facilities Services will select electricians.

Emergency management coordinator

City Coordinator, Office of Emergency Management, 512-974-0461. This group is primarily involved in long term strategic planning and will help review our disaster plan.  Another contact is Officer, Emergency Plans, Kenneth Neafcy, 974-0464.

Exterminator

Andy Howard’s Pest Control

13824 N. IH-35 Frontage Road

Austin, TX  78728

(512) 835-9393

Fire department

Use 911 and then notify Security at 802-7022; Use radio units if necessary

Food services

Facilities services will select food services providers.

Locksmith

Austin Lock Technologies

1008 Mockingbird Dr.

Austin, TX  78652

(512) 280-6264

Cothron’s Locks

509 Rio Grande St.

Austin, TX  78701

(512) 472-6273

Micrographics vendor—handles all Austin American Statesman Microfilm

Note: New contract coming soon-early 2007.

Southwest Micropublishing

2301 Park Hill Dr

Arlington, TX 76012

(817) 480-4646.  Contact Sherry P. Sanders.

And

Southwest Micropublishing

2627 E.Yandell Drive

El Paso, TX 79903

915-562-4525 or 1-800-367-1273

Plumber

Use for larger plumbing breakage. City of Austin will cut off the water main, call 912-6000.

Also:

Roto Rooter

204 W. Powell

Austin, TX  78753

(512) 453-8555

fax (512)-832-9491

Police department

Use 911 and then notify Security at 802-7022.  Use radio units if necessary.

Preservation Services

AMIGOS Preservation Service

14400 Midway Road

Dallas, TX 75244-3509

(800) 843-8482; (972) 851-8000; Fax (972) 991-6061

Daytime procedure: Call main Amigos number and ask for: Elizabeth Klein, ext. 2844 email: klein@amigos.org.  If she cannot help, she will route the call to someone who can.  Always call the main number first in case she is out of the office.  If Elizabeth is out, ask for Gina Minks (2825) IPS Management, Bill Walker (2853) for Imaging Field Services.  Rebecca Elder is the Adjunct Preservation Field Services Officer. Amigos Support Desk (2863).

The after hours emergency number is Elizabeth Klein’s cell phone: 1-469-223-4900. After hours calls may be routed to other staff for additional assistance.

Any time there is a problem reaching someone during the day by calling the Amigos main number, call Elizabeth’s cell phone.

AMIGOS will activate phone help using experts from across the southwest regional alliance group, RAP.  These Alliance members can provide immediate advice.

Security personnel (extra)

Facilities services will select personnel.

Software vendor

Temporary personnel

Facilities services will select personnel

Utility companies:

Electric

Austin Energy.  To disconnect main electrical to the building and information on power outages, call emergency number (512) 322-9100.  An alternative number is the Call Center at 494-9400.  Private Service:  Fox Service Company 512-442-6782.

The first, second, and third floors each have a breaker box which is located in the Archives Stacks area of each floor.  They are located on the North wall and these boxes will allow you to disable an individual circuit one at a time.  Each circuit is individually marked.

The Basement/Ground Floor breaker box is located in the basement mechanical room.  The box is on the West wall.  Again, all circuits are individually marked and each box is gray in color.

The Main Electrical Cutoff Switch is located outside the Austin History Center, next to the Staff entrance door (in between the two library buildings).  It is the large box with the long gray handle.

Gas

There is no gas line in the Austin History Center.  All heating is accomplished by Central Heating.  If needed, for gas related emergencies, call 1-800-959-5325.

Water

City of Austin Water, Dispatch Center, call 512-972-1000.  The Main Water Cut Off valve is located outside the Austin History Center, in a manhole which is located in a North Central direction (just west of the 9th Street Stairs).  To shut off the water, climb down the manhole and turn the large wheel clockwise.

Disaster Recovery Resources

Disaster Recovery Supplies

The following is a list of supplies that can be found in the Austin History Center and in external sources.

Disaster Preparedness Kit

AHC has two disaster preparedness kits:

1.	Supply closet on the Ground Floor of the AHC building

2.	AHC storage area in the basement of the JH Faulk Library

The kit is housed in a large, green or blue portable trashcan with a lid.  The lid should be secured with tape in such a way that it could be readily determined if the lid has been opened.  This will ensure that the disaster supplies are available when needed.  The kit contains the following supplies:

·	barricade tape

·	cotton gloves

·	duct tape

·	dust masks

·	electrical and plumbing tape

·	extension cords (heavy duty)

·	film/print marking pens

·	flashlights (with batteries inside)

·	freezer paper

·	heavy duty work gloves

·	interfacing material (for drying photos)

·	polyurethane gloves

·	heat-resistant masking tape

·	micro-spatulas

·	nametags for volunteers

·	nylon monofilament

·	paper clips (non-rust)

·	pencils

·	pencil sharpener

·	permanent markers

·	Plastic bucket

·	plastic clothes pins

·	plastic sheeting

·	post-it note pads

·	scissors

·	sponges

·	string, packaging tape

·	tool kit

·	trash cans liners

·	wiping cloths

·	writing tablets

q	a copy of the manual is in each supply kit

Bone folders

This tool is used to help separate pages in wet volumes in preparation for interleaving and air drying.  There are two bone folders in the Photo Collection Room and two bone folders in the Archives Room.  If these are unavailable, purchase some from University Products (800-628-1912) or Gaylord Archival (800-448-6160).

Book Trucks

The Austin History Center has several book trucks.  If more are needed, contact Faulk Central Library to borrow book trucks from them.

Boxes/Milk Crates

Boxes and milk crates are used for transporting and storing books for freezing or freeze drying.

The Acquisitions Department of the Austin Public Library receives boxes on a daily basis and often has 30 or more boxes on hand.  They will make as many available as possible to the AHC.

(512) 974-7466

UNISOURCE

210 East St. Elmo Road

Austin TX 78745

(512) 448-9300 or (800) 897-1174

Call the 800 number for cardboard boxes of all sizes.

Rehrig Pacific Co.

625 Mockingbird Lane

Dallas, TX  75247

(214) 678-9398 or (214) 631-7943

http://www.rehrigpacific.com/

They manufacture plastic milk crates.  The company will handle orders of $1,000 or more directly.  Smaller orders are processed through several of their distributors.

Brushes

Used to brush dust from books.  Available from University Products (800-628-1912) or Gaylord Archival (800-448-6160)

Bubble wrap

Used to wrap books.  AHC Exhibits Specialist has bubble wrap or contact Building Facilities Services, 974-7495 or 974-7494

Buckets, plastic garbage cans, trash can liners, rubber gloves, garden hose

Used for setting up a film washing operation and packing film for transport to a processor.  A bucket, latex gloves, and trash can liners can be found in the Disaster Preparedness Kit in the Supply Closet on the Ground Floor.  These supplies also can be purchased from a variety of local sources.  A third option is to consult Building Facilities Services, 974-7495 or 974-7494.

Camera and film

Located in the Photo Room on the first floor near the photo curator's desk in a box marked "Photo".

Cellular Phones

Building Facilities Services, 974-7495 or 974-7494

Chemical Sponge

Dehumidifiers

Building Facilities Services, 974-7495 or 974-7494

Dish pans, plastic

Used for washing of wet or soiled negatives.  Purchase from Target, 2300 W. Ben White 445-2266, or Walmart, 5015 S. IH 35, 443-6601

Distilled water

Used for air drying of wet materials.  Purchase from HEB, 2701 E. 7th St.  478-7328 or at 2400 S. Congress  442-2354

Dollies

Used for transporting items to salvage site. Consult Building Facilities Services, 974-7495 or 974-7494

Dry Ice

This can serve as a temporary means of keeping wet books refrigerated until transport or treatment. Dry ice must never come in contact with skin or photographic emulsions.

City Ice Flash Cubes

2826 Real Street

Austin, TX  78722      (512) 474-4439

Kwik Ice

5715 Burnet Road

Austin, TX  78756

(512) 454-5550 – 24-hour answering service, ask for Buddy.

There is a five pound minimum.

Drying Space

Basement of the John Henry Faulk Central Library.

Dust Masks

Located in Disaster Preparedness Kit in the Supply Closet on the Ground Floor.  Can be ordered from City Central Stores.

Extension Cords

Used for fans or other electrical appliances used during salvage.  Consult Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494.

Fans (including Shop Fans)

Used to keep air moving to prevent mold when air drying damp materials.  Consult Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494.

Flashlight batteries and bulbs

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Fork Lift

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Freezer Paper

Used for separating individual volumes of wet books when packed for freezing.  Freezer paper is available from a variety of sources.  There are two rolls of freezer paper in the Disaster Preparedness Kit in the Supply Closet on the Ground Floor.

Freezer space

Refrigerators located in the staff room, in the first floor kitchen and in the fourth floor break room of Faulk Central Library.

Fungicides

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Garden hose

Used in air drying procedures.  Consult Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Generators and Lights (Portable)

Useful for beginning recovery operations when building power has been interrupted.

United Rentals

609 North Bell Blvd

Austin, TX  78613

(512) 335-0061

Hand trucks

Used for transporting damaged items to the salvage site.  Consult Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Hard hats

Building Facilities Services,  John Gillum or Armando Cubriel 974-7495 or 974-7494

Hardware Stores

Home Depot 5400 Brodie Ln. 892-7887

Or 10107 Research Blvd. 795-8011

Hygrothermograph

Used to measure temperature and humidity in areas of building where damage has occurred and where air drying of materials is taking place.  There is a hygrothermograph in the AHC's outer vault.  If that one is not available, contact the Texas Association of Museums, 3939 Bee Caves Road, Building A, Suite 1B, Austin, Texas 78746, Tel: 512/328-6812, Fax: 512/327-9775.

Kodak Photoflo

Used for air drying negatives and prints.  Available from the AHC Photo Lab or from a photo supplies store (see Disaster Recovery Services section).

Ladders

Located in the basement ground floor custodial closet near the photo lab – get custodial closet key from Building Facilities Services or Security.  One ladder is housed in the Archives Room.

Mops, sponges, buckets, cleaning supplies and brooms

Mops and bucket located behind the elevator on the 1st floor. Mops, buckets, cleaning supplies, and brooms also found in the ground floor basement custodial closet near Architectural Archives. Two sponges also in Disaster Preparedness Kit.

Pallets

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494.

Paper towels (not colored)

Located in the basement ground floor custodial closet in elevator lobby.

Plastic Bags

Located in the basement ground floor custodial closet in elevator lobby.

Plastic Sheeting

Used for protecting materials from water.  Clear polyethylene at least 4 mils thick is best.  There is one roll of plastic sheeting in the Disaster Preparedness Kit in the Supply Closet on the Ground Floor.

Laird Plastics

2200 Denton Drive #103

Austin, TX  78758

(800) 243-4050; (512) 837-2710

Regal Plastic Supply Co.

9311 Metric

Austin, TX  78758

(512) 836-3629

Polyester film (preferably 3 mil)

This film can be used when interleaving wet coated paper volumes.  The AHC has polyester film in the second floor conference room and in the Photo Collection room.  If these items are unavailable, purchase polyester film from University Products (800-628-1912) or Gaylord Archival (800-448-6160).

Polyester web

Used in air drying documents.  Brand name Hollytex available from Talas in New York, New York; phone 212-219-0770

Pumps (submersion)

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Ramps

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Rental Companies

United Rentals  9230 Hwy 290 E.  928-8800

Uhaul  4021 N. IH 35  454-3543

Refrigeration truck

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

High-efficiency particulate air (HEPA) Respirators

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Rubber boots or overshoes

None available on site.

Safety glasses

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Scaffolding

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Shovels

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Spotlights

United Rentals

609 North Bell Blvd

Austin, TX  78613     (512) 335-0061

Trash cans (plastic, small and large)

Building Facilities Services: John Gillum or Armando Cubriel 974-7495 or 974-7494/ located throughout the building.

Unprinted Newsprint

Used for absorbing moisture from damp to moderately wet books.  We have one roll in Supply Closet on Ground Floor.

UNISOURCE

210 E. St. Elmo Road.

Austin, TX  78745

(512) 448-9300 or (800) 897-1174     Call the 800 number for orders

Vacuum/freeze drying facilities

BMS Catastrophes

303 Arthur St.

Fort Worth, TX 76107    (800) 433-2940--For Emergencies

Belfor Recovery Services

2425 Blue Smoke Court South

Fort Worth, TX 76105    (800) 856-3333

Solex Environmental Services

P.O. Box 460242

Houston, TX 77056     (713) 963-8600; cell phone (281) 414-8080

Walkie talkies

Unit 3 by staff copier on first floor; Unit 11 by Public Service Librarian’s office on second floor.  If those are unavailable, consult Building Facilities Services, John Gillum or Armando Cubriel  974-7495 or 974-7494.

Water, drinking

HEB  2701 E. 7th St.  478-7328                 HEB  2400 S. Congress  442-2354

Waterproof clothing

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Wax crayon

Used to identify audio, video, computer tapes and floppy disks while they are being dried.  Available from Office Depot.

Weights

Used when air drying books.  Available from University Products (800-628-1912) or Gaylord Archival (800-448-6160)

Wet/dry vacuum

Used for general cleanup.

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Wheelbarrows

Used for general cleanup. Building Facilities Services, John Gillum or Armando Cubriel  974-7495 or 974-7494.

Wood, lumber

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Worktable and chairs

Building Facilities Services, John Gillum or Armando Cubriel 974-7495 or 974-7494

Disaster Recovery Services and Conservation Contacts

AMIGOS Preservation Service

14400 Midway Road

Dallas, TX 75244-3509

(800) 843-8482; (972) 851-8000; Fax (972) 991-6061

Daytime procedure: Call main Amigos number and ask for: Elizabeth Klein, ext. 2844 email: klein@amigos.org.  If she cannot help, she will route the call to someone who can.  Always call the main number first in case she is out of the office.  If Elizabeth is out, ask for Gina Minks (2825) IPS Management, Bill Walker (2853) for Imaging Field Services.  Rebecca Elder is the Adjunct Preservation Field Services Officer. Amigos Support Desk (2863).

The after hours emergency number is Elizabeth Klein’s cell phone: 1-469-223-4900. After hours calls may be routed to other staff for additional assistance.

Any time there is a problem reaching someone during the day by calling the Amigos main number, call Elizabeth’s cell phone.

Services: AMIGOS will assist with both planning activities and disaster recovery.  They will fax information, provide referrals for resources in the area, and assist on-site as required.  They will assemble teams of preservation experts from across the Southwest who can help during the crisis over the telephone.

Blackmon-Mooring Steamatic Catastrophe, Inc.

303 Arthur Street

Fort Worth, TX  76107

(800) 433-2940 or (817)332-2770.  The 800 number is answered 24 hrs. a day.  Use the On Call Person in case of emergency. Fax (817) 332-6728

Contact person: Paul Schulze

Services: vacuum freeze drying, freeze drying, damage appraisal, inventory, boxing and transportation of materials, document reproduction, restoration/reproduction of microforms and floppy disks, soot and smoke odor removal, fumigation, corrosion control of electronic equipment, debris removal, cleaning of interiors, cleaning and restoration of furnishings.

BMS-Cat.  Specializes in dealing with damage from fire, water, corrosion, and hazardous materials contamination.  According to a company brochure, BMS has over 500 employees, and there are 200 independent contractors in the U.S. and Canada; BMS-Cat can call on these workers to provide the base for any large scale restoration project.  Help for large jobs is also acquired locally.  Emphasis is placed on speed to help minimize damage, and to enable the affected organization to resume operations as quickly as possible.  The company will inventory and box damaged library materials, and can either transport them to their plant for treatment or move their equipment to the disaster site.

Organizations may fill out an Emergency Response form that contains information that would be helpful in expediting action by BMS-Cat.  There is no charge to be pre-registered with the company and the form is not binding.  A list of references is available on request.

Belfor, U.S.A.

2425 Blue Smoke Court South

Fort Worth, TX  76105

(800) 856-3333 or (817) 535-6793.  The 800 number is answered 24 hours a day.

Fax (817) 536-1167

Contact Person:  Kirk Lively

Services:  freeze drying, structural and contents cleaning, mold and mildew treatment, micrographics and magnetic media recovery, photographic restoration, dehumidification, soot removal and deodorization.  DRS specializes in fire and water damage restoration.  The company will arrange to have water soaked books and records transported to their facility in Fort Worth for freeze drying.

SOLEX Environmental Systems

P.O. Box 460242    Houston, TX  77056

(713) 963-8600; cell 281-414-8080    Contact Person: Don Hartsell

Services: moisture removal and freeze drying, vacuum freeze drying, cold storage, moisture removal of floors, walls, furnishings, and computers, dehumidification, removal of airborne contaminants - soot, asbestos, PVCs, air drying of materials, fumigation by arrangement.

SOLEX specializes in fire and water damage recovery.  The company can provide on-site large-scale dehumidification and temporary heating and air conditioning.  The company can arrange for cold storage transportation to their facility in Houston for vacuum freeze drying or freeze drying.  Other services include removal of soot from air conditioning systems and removal of airborne contaminants such as asbestos and PVCs.  References are available on request.

Harry Ransom-Humanities Research Center

P.O. Box 7219  Austin, TX  78713    (512) 471-9117

Contact Person: Olivia Primanis, Senior Conservator, primanis@mail.utexas.edu; or Jim Stroud, Chief Conservator, stroud@mail.utexas.edu

Services: The Conservation Department of the Harry Ransom Center can provide limited advice about treatment for disaster damaged materials.

Library of Congress, National Preservation Program Office, Preservation Directorate

101 Independence Avenue   Washington, D.C.  20540-4500

(202) 707-5213    Mon - Fri 8:00 A.M. to 5:00 P.M.    Contact Person: Merrily Smith

Services: The Library of Congress preservation staff will provide advice and assistance for both disaster planning and for the recovery of water damaged library materials.

Northeast Document Conservation Center

100 Brickstone Square, 4th floor    Andover, MA 01810-1494   (978)470-1010

Contact Person:   Steve Dalton, Director of Field Service, dalton@nedcc.org or kebrown@nedcc.org. Consult web site at: http://www.nedcc.org     Fax (978) 475-6021

Services: The NEDCC will provide emergency assistance over the phone at no charge, and may be reached day or night, seven days a week.  In case of a major disaster, a representative may be sent to provide help on-site.

Eastman Kodak

1 Kodak Plaza     Rochester, NY  14650      (800) 242-2424

Services: Kodak will give advice over the phone on how to treat flood or fire damaged film.

Southwest Micropublishing, Inc.

2627 East Yandell Avenue    El Paso, TX  79903    (800) 367-1273 (Sales)

Contact Person:  Victor Rivera  800-367-1273

Services: Southwest Micropublishing's vast experience in newspaper preservation is now focused on the backfile microfilming of bound and unbound, brittle, water-stained, and light-damaged pages.  The responsibility of microfilming currently published newspapers and the fulfillment of their microfilm subscriptions has been taken over by Heritage Microfilm, Inc.; see below.

Heritage Microfilm INC

4049 21st Avenue SW    Cedar Rapids, Iowa 52404

Contact Person:  Marilyn Gill  888-870-0484 or mgill@heritagemicrofilm.com

Services:  Replace Austin American-Statesman microfilm that has been damaged.

Photographic Processing

Black and White:  Austin Prints Photo Lab

1700 S. Lamar   Austin TX  78704        512-441-7591

Color:  		   Holland Photo Imaging

1221 S. Lamar Blvd.   Austin, Texas 78704      512-442-4274

Photo Supplies

University Co-op

2244 Guadalupe    Austin TX  78705        512-476-7211 xt. 8103

Camera Co-op

2620 S Lamar Blvd Ste C    Austin TX 78704-5170      512-804-2667

American Institute for the Conservation of Historic and Artistic Works (FAIC)

1717 K St. N.W., Suite 200      Washington, D.C.  20006

Telephone (202) 452-9545      Fax: (202) 452-9328

Email address: Info@aic-faic.org     Website:http://aic.stanford.edu

Services: Will provide a list of conservators (but not recommendations.)

Computer data and hardware recovery

Consult APL Technical Support, specifically Joe Faulk  ext. 7304 or Jim Greco  ext. 7454

Federal Emergency Management Agency

FEMA Region VI (Federal Regional Center)

800 North Loop 288    Denton, TX 76201-3698

Telephone: (940) 898-5399      Fax: (940) 898-5325

Local Contacts

Other individuals and/or organizations to provide information or assist in cleanup:

Alan Van Dyke

Harry Ransom Center, University of Texas

(512) 232-4620, alan@mail.utexas.edu

Ellen Cunningham-Kruppa

School of Information, University of Texas

(512) 471-8287, e.cunnk@mail.utexas.edu

David Gracy

School of Information, Gov. Bill Daniel Professor in Archival Ent., Ph.D, University of Texas

(512) 471-8291, gracy@ischool.utexas.edu

Lori Curtis

Head of Special Collections & University Archives, McFarlin Library

University of Tulsa, 600 South College Avenue Tulsa, OK 74104

(918) 631-2882    lori-curtis@utulsa.edu

RAP (Regional Alliance for Preservation): their website is: http://www.rap-arcc.org/.

For TLA (Texas Library Association) funding, see: http://www.txla.org/groups/committees/relief/index.html.

Fire

Prevention Activities

Fire prevention should include the following activities:

*	Instruct staff and volunteers in the emergency routine that should be followed when a fire is discovered.

*	Make certain all have read the Security Manual and the Disaster Manuals as part of their job orientation.

*	Staff training and instruction in how to use portable fire extinguishers.

*	Annual fire inspections by an outside fire marshal and disaster team leader.

*	Risk Assessment Form for fire should be completed annually.

*	Attention by the fire marshal to special hazards that might be present.

*	Special attention to any jobs performed by Building Facilities Services workers or outside contractors in which there is a possible fire hazard (e.g., welding, and cutting operations, use of flammable solvents).

*	Conduct a closing time inspection each day.

- Waste paper and other combustible trash should be placed in a metal can with a tight-fitting lid.

- Trash should be removed from the building daily.

- Ensure that coffeemakers, typewriters, or other electrical equipment have been turned off.

- Fire doors and smoke barrier doors should be closed.

- Ensure that doors and windows are secured.

- Ensure that people who should leave the building are gone.

Watch for these fire hazards:

*	smoking in the building

*	combustible draperies and carpet

*	Christmas trees and other decorations

*	flammable liquids (e.g., cleaning supplies, paints, other chemicals)

*	No serviced or not working HVAC equipment

*	unclean air filters

*	makeshift wiring, extension cords longer than 6 feet, electrical cords running under carpets

*	fire and smoke doors left open

*	unattended space heaters

*	construction debris

*	blocked aisles and doorways

Emergency Procedures

Basic Fire Procedures

In case of a fire:

·	Remain calm.

·	Contact the Fire Department.

·	If the fire is small, try to extinguish it with the proper type of extinguisher or other method.  Do not jeopardize personal safety.

·	Do not allow the fire to come between you and the exit.

·	Disconnect electrical equipment if it is on fire and it is safe to do so.

·	Notify the supervisor and evacuation coordinator, if possible.

·	Evacuate if you cannot extinguish the fire.  Assist disabled persons.

·	Do not break windows.

·	Do not open a hot door.  (Before opening a door, touch it near the top.  If it is hot or if smoke is visible, do not open.)

·	Do not use elevators.

·	Do not attempt to save possessions.

·	Go directly to the assembly area.

·	Do not return to the affected area until told to by appropriate authorities.

·	Do not spread rumors. National Park Service. Disaster Plan. [Web page].

When You See a Fire

Pull the fire alarm nearest you.  Call Security immediately.  Use the radio if it is nearby, otherwise call the switchboard (x7300) from a telephone in an area removed from the fire and have them page security as an emergency.  Also dial 911 to report the fire, giving your location (Austin History Center, 810 Guadalupe).  The Fire Department will coordinate calls.  They would rather come in error than not be notified on time.

One radio unit is located in the General Collection Stack Area – Unit #3.

One radio unit is located in the 2nd Floor Staff Area – Unit #11.

If the fire is small and confined to a single object such as a wastebasket, fight it with a hand-held fire extinguisher until further help arrives.  Fire extinguisher locations are designated on evacuation floor plans in each building.

If the fire is not extinguished immediately, pull fire alarms and follow evacuation procedures in Floor Plan Maps.

When You Hear the Fire Alarm Evacuate the Building Immediately!!

Do not wait for verification of the fire.  Time is critical.  Begin evacuation procedures immediately.

The person in charge should call security on the radio to report the alarm and announce the location of the fire, if known.  The person in charge should keep the walkie-talkie for the duration of the emergency. Reference staff should carry the sign-in board to the designated evacuation meeting place, Wooldridge Park gazebo.

ALL patrons and staff must evacuate the building according to evacuation floor plan.  Assemble in Wooldridge Park at the gazebo, one block north of the History Center.

Minimal staff on evenings and weekends could make the assignment of duties even more strained.  Do your best.  The person in charge at any given time is (in descending order of presence, depending on who is present) the AHC Manager, AHC Asst. Manager, the Public Services Librarian, or the senior staff member scheduled in the Reading Room.

Use the following announcement; repeat twice:

"Your attention please.  Everyone must evacuate the building immediately.  Please remain calm.  Exit immediately using the doors (in the lobby and/or at the end of the East Hall).  Assemble in the Wooldridge Park at the gazebo across the street to meet family members or seek medical assistance.”

Lives are more important than belongings.  The Fire Marshal estimates that a fire on the first floor of the AHC would take only three minutes to engulf the entire floor.  This means that you won't have time to open lockers for patrons or get your own belongings.  Be prepared to be firm.

Handicapped patrons might need extra assistance:

*	The physically impaired might need extra help using the wheelchair lift if it is accessible.  If it is not accessible, Fire Department personnel will assist them when they arrive.

*	Visually or hearing impaired patrons should have staff members assigned to help them and escort them out of the building if necessary.

For Evacuation

*	Do not use the elevator.

*	AHC Staff is responsible for "sweeping" the first, second, and third floor of the AHC.  Security is responsible for the ground floor.

*	As each room is evacuated, close the door without locking it.

*	Use the 9th St. or Guadalupe St. entrances to exit the building.

*	If the fire blocks the Reading Room door so that evacuation through the lobby is impeded, open the middle window in the Reading Room and either jump to the grass below or hang a sheet or some cloth out the window to draw the firefighters’ attention.  When they see the cloth hanging out of the window, the firefighters can lean a ladder against the window to assist with evacuation.

*	If a fire is blocking escape from the Second Floor, there is an escape hatch inside the office at the head of the stairs.  There is also a white sheet by the magazine stacks for hanging out the windows-facing south-to get firefighters’ attention.  The firefighters should then place a ladder beneath the window to assist staff in evacuating the area.  There is also a metal chain evacuation ladder kept near this window for staff. to use.

*	If the alarm goes off when the public doors are still locked, use either the stairs by the elevator or the stairs in the stacks, or unlock a public door.  Security leaves a key in one 9th Street door and the Guadalupe Street door when they open the building for staff in the morning, and remove the key when they open the doors for the public.

*	All staff should assemble in Wooldridge Park as they evacuate the building.

*	Find a firefighter with an orange, red or white helmet (these will be people directing the firefighting effort) and let them know that everyone was evacuated from the building successfully.

*	Medical staff will go to Wooldridge Park to treat injured people.

It is possible that the AHC may be evacuated if there is an emergency in the John Henry Faulk Library.  If instructed, be prepared to begin evacuation procedures without an alarm sounding in this building.

If Security staff informs AHC that the alarm has proven to be an error, make the following announcement:

"Please excuse the alarm.  There is no emergency."

Repeat several times at intervals as necessary.

The person in charge should:

*	Inform any people using the meeting rooms that they must evacuate the building.  Notify the library administration of the emergency.

*	Determine which staff and volunteers are in the building (using the sign-in board) and make sure they are informed.

*	Make sure someone takes the sign-in board to Wooldridge Park.

*	Assign staff to assist any handicapped customers who may need help evacuating.

*	"Sweep" the first, second, and/or third floors to make sure all people have evacuated.

*	Assign people to stand at both the 9th Street and the Guadalupe Street doors to keep customers from entering the building until the "all-clear" notice is given.

*	Go to the Maintenance Entrance (in the parking lot) to meet Fire Department Personnel

*	Take a head count at Wooldridge Park to make sure that all staff is accounted for.

*	Designate other staff members to do any of the above, as necessary.

Recovery Procedures

Items not directly damaged, which have soot deposits but no evidence of charring or heat damage, may be cleaned.  There are commercial services which specialize in the soot removal and deodorization of materials as well as rooms and furnishings.  They may be utilized if their services are deemed cost-effective.  (See Disaster Recovery Services and Conservation Contacts in Introduction Section of this plan.)

If appropriate, books may be sent to a library bindery to have their cases removed, text block trimmed, and new covers put on.

Charcoal and/or baking soda can be used to deodorize fire-damaged materials.  After cleaning and drying is complete,  place briquettes or bowls of baking soda in the area.

Eastman Kodak will give advice over the telephone on how to treat fire damaged film.

FIRE DAMAGED MATERIALS

In case of fire, all burned or charred materials will have to be removed from the area before ventilation of smoke and air cleaning can be effective.  Those items obviously beyond salvage can be placed on book trucks or in boxes or garbage bags and taken to another location (preferably outside) for bibliographic control procedures.  Those which can be salvaged can be removed by book truck to the recovery area.

Binding Fire Damaged Books

Charred items which are to be rebound will need special handling before being sent to the commercial bindery.  Follow these instructions for sending fire damaged materials to be rebound:

1.	Fire damaged materials should be boxed separately from other binding shipments and marked accordingly.

2.	Periodicals should be kept separate from monographs.

3.	All charred or burned covers should be removed before shipment.

4.	Be sure the call number is written on the verso of the title page.

5.	Any book requiring special treatment (do not trim, specific buckram color, etc.) should be brought to the attention of the commercial bindery.

Smoke and Soot Removal

If the only damage to books and papers is soot on the outside, it may be possible to remove most of it by cleaning with a chemical sponge.  The chemical sponge does not contain chemicals which assist in the removal of dirt and odors; the name refers to the process of manufacturing a sponge that is much more dense than usual.  The sponges can be cut down to fit the cleaner's hand, and can be washed and reused several times.

To clean a book, hold the book tightly closed.  Use a gentle stroking motion in one direction away from the spine toward the fore edge on the head and/or tail, and the same kind of technique on the fore edge, spine and covers.  Continue wiping until no more soot or debris can be removed without damaging the surface area.

Deodorizing

Charcoal and/or baking soda can be used to deodorize fire-damaged materials.  Place charcoal briquettes and/or bowls of baking soda in the area to absorb the odor.  If a small number of books are affected, a clean metal barbeque or similar container can be used.  Spread briquettes in the bottom and place books on a rack over them.  Close the lid and wait two or three days or until the smell can no longer be detected.  The thymol chamber can also be used for this purpose.

Ozone

Ozone can remove odors but must be used with care and should not be used with books or papers that are wet or damp.  Ozone can combine with water molecules to form hydrogen peroxide (bleach) and can cause discoloration and weakening of some materials. Ozone will break down cellulose (e.g. paper) molecules and cause them to age more quickly. Ozone should not be used in occupied areas because high concentrations can result in respiratory irritation.  From Illinois State University Libraries Disaster Plan. [Web Page]. http://palimpsest.stanford.edu/bytopic/disasters/plans/isudis.html [Accessed December 16, 2003.]

Access

Where water damage has resulted from fire-fighting measures, cooperation with the fire marshal, and health and safety officials is vital for a realistic appraisal of the feasibility of a safe salvage effort. Fire officers and safety personnel will decide when a damaged building is safe to enter. In some cases, areas involved in a fire may require a week or longer before they are cool and safe enough to enter. Other areas may be under investigation when arson is suspected. There may be parts of a collection that can be identified early in the salvage planning effort as being especially vulnerable to destruction unless they receive attention within a few hours after the fire has abated. If the fire marshal appreciates such needs, he may be able to provide means of special access to these areas even when other parts of the building remain hazardous.

Perhaps the most important and difficult decision to make after an assessment of damage has been made, is whether to remove the wettest materials first or to concentrate on those that are only partially wet or damp. If the majority is in the latter category the best course may be to recover these first since they may develop mold if they are left in dank and humid conditions while the wettest material is removed. A balance must be struck between reducing the moisture content in the affected areas and the time involved for the safe removal of the majority of the collections in the best condition. To remove the wettest material first will obviously lower the moisture content, but it is often the case that this can be difficult and time consuming owing to the fact that shelves will be jammed with swollen wet books and boxes that may require special equipment to free them. The aim is always to recover the majority of the collection in the best condition to avoid additional harm and costs brought about by post-disaster environmental damage.

Once all entrances and aisles have been cleared, in addition to the above considerations, the most important collections, including rare materials and those of permanent research value, should be given priority unless other material would be more severely damaged by prolonged exposure to water. Examples of the latter are books printed on paper of types widely produced between 1880 and 1946, now brittle or semi-brittle. However, materials in this category which can be replaced should be left until last. National Park Service. Disaster Plan. [Web page].

For Further Reading

Morris, John.  1979.  Managing the Library Fire Risk.  2nd ed.  Berkeley, CA:  Office of Risk Management and Safety, University of California.

Wilson, J. Andrew.  1989.  “Fire Fighters.”  In Museum News.  November/December:  68-72.

Water

Prevention Activities

Reducing the risk of fire also reduces the risk of damage from water.  If firemen never have to fight a fire within the Austin History Center, then a large scale soaking of the collection is unlikely.  However, there are other significant water hazards within the building.

Plumbing - All water pipes leading to water fountains, sinks, toilets, automatic dishwashers, and ice makers should be regularly inspected for signs of corrosion, specifically at joints.  The general staff should be aware of the location of all water pipes in ceilings and walls as well as their corresponding shut-off valves.  This information should be documented and periodically reviewed with staff members.

Ceilings - Materials and equipment should not be stored beneath nor next to water pipes leading to such areas as janitor's closets or rest rooms.  Since, however, this is not feasible at the Austin History Center, the ceilings of rooms on the ground floor beneath the restrooms should be inspected for rust discoloration, loose plaster or mold; signs of a pipe with a slow leak.  Also due to this increased water risk, plastic sheeting should be kept readily available.  ALL MATERIALS SHOULD BE STORED AT LEAST 4 INCHES OFF OF THE FLOOR IN ALL AREAS.  This prevents damage from minor flooding and damage by indirect splashing.

HVAC - Pipes supplying water to and from the HVAC system should be monitored, including water supply lines to steam humidifiers for signs of corrosion and leaks.

Roof - The Austin History Center has a flat tar and asphalt roof that is internally drained to storm sewers.  Statistically, no flat roof is completely flat and some perverse law of fate suggests that all flat roofs will eventually settle enough to cause water to flow away from roof drains.  Periodically, after a heavy rain, the roof should be inspected to discover if water is pooling in areas away from roof drains.  An ideal place from which to inspect the roof is the acquisitions department of the Main Library.  The roof should be inspected to ensure that roof drains are clear of leaves and other debris.

Doors and Windows - Doors and windows should be properly weather stripped to ensure that water cannot enter.  Window sills and door sills should be regularly inspected for signs of leaks.

Emergency Procedures

Staff and patrons must not enter an area that is flooded until Building Facilities Services has disconnected the electricity.  There is danger of severe electrical shock.

1.	Call Building Facilities Services and have them disconnect electricity.  The main electrical cut-off switch is located outside the AHC, next to the Staff entrance door.  It is the large box with the long gray handle.

2.	Call the Recovery Team Leader, Sue Soy (327-8413).

3.	Locate the water source and stop water flow.  If the flooding is caused by a malfunction within the building, the main water cut-off valve must be activated.  Notify the City of Austin Utilities Department (912-6000).  The valve is located outside the AHC, in a manhole next to the 9th Street stairs.  To shut off water, someone must climb down the manhole and turn the large wheel clockwise. Hopefully, someone from the City can do this, but if someone in the collection can respond quickly, damage can be minimized.  If water is coming from above, cover materials/equipment with plastic sheeting, if available.  If not, cut up plastic garbage bags to use in place of sheeting.  If the water is localized, remove materials from the path of the flow.  Remove materials from the floor if they are dry and place in a safe location.

4.	Place plastic buckets or wastebaskets under leaks.  Buckets can be used to collect water dripping off of plastic sheeting.

5.	Mop up water with a mop and bucket and/or a wet-dry vacuum.

6.	Turn off all heat.  Reduce temperature as much as possible.  Keep air conditioning systems operable and set at lowest temperature possible.  Use portable air conditioners where necessary.  If necessary to open windows and doors for air circulation, arrange for security of the collections.  Use fans to aid circulation.  Use dehumidifiers with fans where necessary.  If power is off, use portable generators for electrical services.  All lines must be waterproofed and grounded.  Use hygrothermographs to monitor affected areas or arrange for an outside resource to monitor the temperature and humidity. From University of California at Davis Disaster Prevention, Preparedness and Recovery Plan [Web page]

http://www.lib.ucdavis.edu/preser/disaster/ [Accessed December 16, 2003]   Conditions are acceptable when temperature is less than 75F and relative humidity is less than 65%.  Mold and mildew will flourish at higher levels.

7.	Take photographs to document damage.

Recovery Procedures

With items properly stored to prevent further damage, the Recovery Team will determine what drying method to use.  There are five to choose from: air drying, dehumidification, freezer drying, vacuum thermal drying, vacuum freeze drying, and conservation consultants should be contacted to advise on the best procedure for the situation.  A table of "Disaster Recovery Procedures" is provided at the end of this section.

Cleaning and Drying

Paper is very fragile when it is wet. Handle it carefully. In some cases it may be desirable to remove caked on mud and dirt. Dirt left by receding floodwaters may be contaminated. Precautions such as the use of rubber gloves should be taken. If items are still wet, agitating them in a bath of clear water will remove excess dirt. This treatment should never be attempted for images which are blurred, feathered, or faded as a result of flood damage.  National Park Service. Disaster Plan. [Web page].

Air Drying

Wet books, documents, or photographs which cannot be air dried within two days should be frozen to inhibit mold growth. Drying rooms should be set up away from disaster area. Drying rooms should have the capacity to maintain a constant relative humidity of 25 - 35 percent and a temperature of between 50 and 65 degrees F. The room should be monitored to verify these conditions. Drying rooms must be kept free of wet salvage debris. University of California at Davis Disaster Prevention, Preparedness and Recovery Plan [Web page]   Circulating air will effectively dry most items. Physical distortions may result, but document information will be saved. To provide optimal air drying conditions, fans should be positioned for maximum air circulation (do not aim airflow directly at drying materials). Blotting material for air-drying should be clean and absorbent. Options include: blotter paper, unprinted newsprint paper, paper towels, rags, mattress pads, etc. Screening material (such as window screens) well supported and stacked with space between them provide an excellent compact drying surface. The porous surface assists air circulation and promotes drying.

Without intervention glossy materials such as paperback book covers, magazines, art books, etc. are likely to stick together. If they are highly valued, these items should be the first priority for salvage. Loose glossy materials should be spread out in one layer for air-drying.  Bound glossy materials must be interleaved between every page to prevent sticking. Volumes of glossy paper dried in this way may suffer considerable physical distortion.  National Park Service. Disaster Plan. [Web page].

Books

Air-Drying Saturated Volumes Not on Coated Paper Stock

Prepare worktables by covering them with plastic sheeting under absorbent toweling (paper towels or unprinted newsprint). Squeeze book gently and with even pressure to remove excess water and to reshape binding. Stand book upright, head end down (upside down).  DO NOT OPEN PAGES.  Covers may be opened slightly to support text block. Plastic film or freezer paper may be placed between the cover and the text block to prevent staining from binding dyes. To support book while draining, use 1/4" styrofoam cut into small pieces 3/4 inch wide and slightly longer than the thickness of the book block under the front edges (boards) of each book.  This will keep it balanced in an upright position, tilted slightly backwards. Change absorbent toweling frequently.  Remove wet paper from area. University of California at Davis Disaster Prevention, Preparedness and Recovery Plan [Web page]

Air-Drying Wet Volumes Not on Coated Paper Stock

Carefully open volume to less than a 30-degree angle, still in an upright position (head end down). Interleave with unprinted newsprint or paper toweling. Begin interleaving from the back, placing interleaving sheets at intervals of 25 leaves (50 pages), unless it appears this will distort the volume. Place volumes in the path of circulating air. Change the interleaving material frequently, removing wet paper from drying room to dry elsewhere.  Reverse position of volume each time interleaving is replaced, alternating between head end up and head end down.  Do not reuse interleaving sheets unless they have been impregnated with a fungicide. As the book dries, it can be opened flat on the spine and interleaved more closely.  Interleaving should not exceed 1/3 the thickness of the volume. Continue to change absorbent paper on worktables.  Ibid.

Air-Drying Slightly Damp Volumes or Volumes with Wet Edges (Not on Coated Paper Stock)

Stand volume on its head and fan open slightly.  Paperback books can support each other with a barrier between them or they can be wedged with styrofoam pieces. Place volumes in the path of circulating air. Lightweight volumes (less than 6 pounds) may be hung on lines to dry if the paper feels damp but not wet, and if the book can be opened easily throughout. Use monofilament nylon lines, not more than 1/32" in diameter, and not more than five or six feet long, spaced approximately one-half inch apart. Three lines are enough for a volume of ordinary thickness (up to 1 1/2 inches).  Thicker volumes will require more lines, but no volume heavier than six pounds should be hung up. Do NOT line-dry a saturated volume: the monofilament line will cut through the wet paper. When almost dry, lay volumes flat and place weights on covers to reduce distortion in boards. Ibid.

Air-Drying Volumes on Coated Paper Stock

Coated papers are the most vulnerable to complete loss and should not be permitted to begin drying until each volume can be dealt with under carefully controlled conditions. The period between removal and freezing is critical. It may be necessary to re-wet them with clean cold water until they can be frozen. During the aftermath of the Corning Museum Library river flood of 1972, it was found that the highest percentage of water damaged books were printed on coated stock papers and that when they were frozen in the wet state most were dried successfully by freeze-drying. National Park Service. Disaster Plan. [Web page].

Wet coated paper stock should be handled with care, as the print will slide off the wet page if rubbed.  Do not allow material to dry or it will bond together.  If freezing wet volumes on coated paper is not an option, try air-drying.  To dry wet items printed on coated paper stock, every page must be interleaved.  To separate saturated pages, follow these instructions:

1.   Place a sheet of polyester film on top of the first page and a sheet of interleaving material to the left of the first page.

2.   Rub gently with a bone folder to create the surface friction which will allow the wet paper to adhere to the film.

3.   Turning film (with page attached) to your left, insert interleaving material behind the page.

4.   Carefully remove polyester film.  Turn page using interleaving material.

5.   Place the sheet of film on top of the following page, repeating earlier steps until all pages have been separated. If material is wet but not saturated (pages can be opened safely by hand) it may be interleaved without using the polyester film.  Every page must still be interleaved. Materials may be frozen at this point.  If they are to be air-dried, the interleaving materials must be changed every two hours.  Do not reuse interleaving sheets unless they have been impregnated with a fungicide. University of California at Davis Disaster Prevention, Preparedness and Recovery Plan [Web page]

Documents

Drying Single Sheets

When single sheets are found in groups, as in file cabinets or boxes, it is best to freeze them as they were found rather than attempt to separate them.  Do not remove sheets from file folders or document boxes -- they will separate easily when vacuum- or freeze-dried. Should it be necessary to separate a mass of papers for hand-drying, the following procedures are necessary:

1.   Place a sheet of polyester film on top of a stack of wet, unbound papers.

2.   Rub gently with a bone folder to create the surface tension which will allow the wet paper to adhere to the film.

3.   Peel back the film with a single wet sheet attached and place it, polyester side down, on a table.  Place a piece of dry polyester web over the wet sheet.

4.   Turn so that web side is down and remove polyester film, replacing with a second piece of dry polyester web.

5.   Continue repeating the process, separating the wet sheets one at a time, interleaving with polyester web. Materials may be air-dried or frozen at this stage.

6.   Air-dry the sheets (supported by the two pieces of polyester web) by placing them on absorbent paper on tables or on top of closely spaced monofilament lines. By the time 100 sheets have been separated, the first  sheets will be dry.

7.   Air should be kept circulating, but fans should not blow directly on the materials.

8.   Papers may be flattened when almost dry by placing them between two sheets of blotting paper and applying even pressure with weights. Ibid.

Photographs, Negatives, Motion Picture Film

Photographic materials should not be allowed to dry in place after they become wet as they will stick to their envelopes or to each other.  Separating them after they have dried together will result in damage to the emulsion or the image.  The following recommendations are summarized from the work of Klaus Hendriks and Brian Lesser on the salvage of water-damaged photographic materials:

1. Keep immersion time to a minimum.

2. Keep water temperature low. (65° or below)

3. Freezing of photographs retards further deterioration.

4. As films appear to be more stable, salvage prints first.

If personnel and time are available, salvage methods in order of preference are:

1.  air-dry (without freezing)

2.  freeze; thaw; air-dry

3.  freeze-dry in a vacuum chamber

Vacuum freeze-drying (as is done with printed materials) is not recommended due to blocking or sticking of gelatin layers. . National Park Service. Disaster Plan. [Web page].

Glass Plate Negatives

1.	Handle with care. Glass plate negatives are heavy and water may weaken boxes.

2.	Pack horizontally in padded crates.

3.	Air-dry immediately. NEVER FREEZE.

4.	Dry face up.

5.	Remove paper envelopes. If paper sticks to emulsion, soak in cool water and gradually peel paper away from gelatin.

Framed Items

Remove the backing material from the frame. If the item is not stuck to the glass, carefully remove it from the frame and air dry. If the object appears to be stuck to the glass, do not attempt to remove it from the frame. Dry intact with the glass side down.

Occasionally object damage is irreversible. The treatment of items of high monetary, historic, or sentimental value should only be performed in consultation with a conservator. Decisions about the treatment of materials belonging to an institution should only be made by appropriate personnel. The American Institute for Conservation (202-452-9545) maintains a referral list of conservators who will be able to provide guidance for treating private collections. From National Park Service. Disaster Plan. [Web page].

Archival Box Files

Archival box files often fare better than book material because their boxes are made of porous board stock which can be expected to absorb most of the water, protecting the contents inside. This would not be the case of course if they were completely immersed under water for many hours. During recovery, the contents of each box should be carefully inspected and the box replaced if it is water saturated. Failure to do so will increase the risk of physical damage as boxes collapse from pressure during recovery, shipment and cold storage.  Ibid.

Floppy diskettes:

For disks that are not thoroughly soaked (water does not drip off), use a hair dryer.  Use the "Air" setting, not "Heat". Hold sleeve slightly away from disk. Dry all sides of  sleeve and disk. When dry, make copy of diskette. Disaster Preparedness and Training Plan for Volpe Library Tennessee Technological University [Web page] http://www2.tntech.edu/library/disaster/disaster_plan.html

Maps, Blueprints, Oversized Materials

1.	Sponge standing water out of map drawers.

2.	Remove the drawers from the cabinets.

3.	Pack materials in map drawers, bread trays, flat boxes or poly-covered plywood.

4.	DO NOT try to separate.

5.	Bundle rolled maps very loosely in small numbers.

6.	Freeze-dry only.

7.	Freeze within 48 hours. Ibid.

Media

Audiocassettes:  Replacement may be less expensive than recovery.

A. Water Damage

1.	DO NOT FREEZE TAPES.

2.	Tapes may sit in cool, clean water for a short period of time.

3.	Clean the outer surfaces of the tape pack and the reel.

4.	Do not open a cassette tape unless the inside is contaminated.

5.	Support cassettes vertically in plastic crates or cardboard cartons, or lay them on sheets of newsprint spread over plastic covered tables. Do not put excessive weight on sides of cassettes. The longer they are wet, the greater the damage.

6.	Air-dry in a reduced humidity environment if possible. If copyright permits, rerecord tape after drying.

7.	Do not attempt to play damaged tapes because they can damage the equipment on which they are played.

8.	Inspect collection over the next year to check for outbreaks of mold.

B.	Contamination with dirty water

1.	Dismantle the cassette case.

2.	Wash tape, wound on its reel, with a small amount of mild detergent (dish washing liquid that is dye- and perfume-free) and water.

3.	Blot tape with lint-free cloth, taking care to not harm edges.

4.	If the reels are dirty, remove the tape and clean or replace reels.

5.	Return the tape to its box after the box is dried or replaced.

6.	Handle as for water-damaged tapes. Ibid.

Compact Discs/CD-ROMs /Laser-Discs

A.  Water-Damage

1.	Hold the disc by the outer edges.

2.	Using distilled water, and working out from the center in a straight line, wipe off water or dirt with cheesecloth or other soft, dry, lint-free cloth.

3.	Air-dry. Do not use a hairdryer to remove moisture or to blow off dirt. Ibid.

Digital Audiotapes

DO NOT FREEZE ANY TAPES (including U-Matic tapes)

A.  Water Damage

1.	Tapes may sit in cool, clean water for a short period of time.

2.	Do not open a cassette tape unless the inside is contaminated.

3.	Clean the outer surfaces of the tape pack and the reel.

4.	Support tapes vertically, or lay them on sheets of newsprint spread over plastic covered tables, and air-dry.

5.	Dry the tapes in a reduced humidity environment, if possible.

6.	If copyright permits, rerecord tapes after they are dry.

B.   Dirty Water Damage

1.	Dismantle the cassette case and wash tape, wound on its reel, with a small amount mild detergent (dish washing liquid that is dye- and perfume-free) and water.

2.	If reels are dirty, remove the tape and clean or replace reels.

3.	Return the tape to its box after the box is dried or replaced.

4.	If copyright permits, rerecord tape after drying.

5.	Pack vertically into plastic crates or cardboard cartons. Do not put excessive weight on sides of cassettes. The longer they are wet, the greater the damage.

6.	Do not attempt to play damaged tapes because they can damage the equipment on which they are played.

7.	.Inspect collection over the next year to check for outbreaks of mold.

8.	In case of mold, wet film with rubber gloves, dry with cotton gloves.

9.	Replacement may be less expensive than recovery.

Records

A.  Water Damage

1.	Wash with distilled water and dry with a soft lint-free cloth following the grooves of the    record.

2.	If labels come off, use a grease pencil to write the number or call number on the center of the record.

3.	Hang or stand the jackets to dry.

4.	Put records in new sleeves and reuse jackets if possible.  Ibid.

Slides

A. Water Damage

1.	Slides which cannot be handled immediately should be placed in zip-lock bags filled with COLD distilled water and refrigerated. If refrigeration is unavailable, add ice cubes to the zip-lock bags. Slides should not be immersed for more than 48 hours.

2.	DO NOT VACUUM FREEZE DRY.

3.	Slides should be sent to a processor or frozen if wet longer than 48 hours. Freeze in mounts. Frozen slides may be air-dried later.

4.	When ready to air-dry, remove cardboard mount. Do not remove plastic mounts.  Rinse slides with cool, distilled water.

5.	Save mounts until information can be transferred.

6.	Air-dry as soon as possible. Air-drying requires a cool temperature, low humidity environment. Fans should be used to circulate the air, but not to blow directly onto drying material. Ibid.

Videocassettes

1.	Do not freeze cassettes.

2.	Cassettes may sit in cool, clean water for up to one week.

3.	Do not open a cassette case unless the inside is contaminated.

4.	Clean the outer surfaces of the cassette and the reel.

5.	Support tapes vertically in plastic crates or cardboard cartons, or lay them on sheets of newsprint spread over plastic-covered tables, and air-dry.

6.	Dry the tapes in a reduced-humidity environment if possible.

7.	Clean and dry videocassette boxes. Re-label if necessary.

8.	Do not attempt to play damaged tapes because they can damage the equipment on which they are played.

9.	Inspect collection over the next year to check for outbreaks of mold. Ibid.

How Water Affects Books and Unbound Materials

Paper absorbs water at different rates depending on the age, condition, and composition of the material. Thus, some under standing of the mechanism of swelling action, as well as the development of mold, is essential to planning a successful salvage operation. In addition, when large collections are at stake, it is useful to be able to calculate in advance the approximate amount of water which will have to be extracted in a drying process. This will provide helpful data when selecting an appropriate drying method. Of equal importance is some knowledge of the length of time each type of material can be submerged in water before serious deterioration occurs. National Park Service. Disaster Plan. [Web page].

Estimating Water Absorption

Generally speaking, manuscripts and books dated earlier than 1840 will absorb water to an average of 80 percent of their original weight. Some may absorb as much as 200% of their original weight. Since there is a greater concentration of proteinaceous material and receptivity to water in such early books and papers, they are especially vulnerable to mold when damp. Modern books, other than those with the most brittle paper, will absorb an average of up to 60 percent of their original weight. Thus, in estimating the original weight of a collection, if one assumes an average of four pounds per book when dry for 20,000 books in each category, drying techniques must be capable of removing approximately 64,000 pounds of water from the former  material and 48,000 pounds from the latter.

The major part of all damage to bound volumes caused by swelling from the effects of water will take place within the first four hours or so after they have been immersed. Since the paper in the text block and the cardboard cores of book bindings have a greater capacity for swelling than the covering materials used for the bindings, the text-block of a soaked book usually expands so much that the spine assumes a concave shape and the fore-edge a convex shape, thus forcing the text block to become partially or completely detached from its binding. The board cores of bindings absorb a great amount of water in such circumstances and are usually the source of mold development between the board papers and fly leaves. This is especially apparent when the area in which water damage has occurred begins to dry out and the relative humidity falls below 70%.

Although it is obviously important to remove as much moisture as possible from the environment, it is essential that the water content of the material be monitored because this will remain dangerously high, long after the area is apparently safe. Action taken to salvage the material should therefore be governed by the water content of the material and not by the relative humidity of the area. A water moisture meter, such as an Aqua Boy can be used to measure the water content inside books and box files. If such an instrument is unavailable a crude but quite effective way is to use a mirror within but not touching the text block. Condensation will cloud the mirror. A water content measuring less that 7% is considered dry.

Leather and vellum books, especially those of the 15th, 16th, and 17th centuries, can usually be restored successfully if they are dried under very carefully controlled procedures. Such materials are usually classified as rare and should be treated accordingly by not mixing them with less rare materials during preparations for salvage, stabilization and drying. The advice of a certified book conservator may be essential in order to safely carry out the most appropriate methods. If the material is frozen, freezer paper should be used between each volume to prevent sticking. (Refer to the section on freeze-drying for the special requirements needed for drying this type of material).

Unfortunately, modern manufacturing processes so degrade the natural structure of leather that, once water soaked, book covers are often impossible to restore. Some leather bindings will be reduced to a brown sludge, while others will severely shrink. Swelling of covering materials, such as cloth, buckram, and certain plastics is negligible, in some cases shrinkage occurs. Book covers, however, which are made of a highly absorbent cardboard, will absorb water to a greater degree than an equivalent thickness of text block. Some book covering materials which have already deteriorated will absorb water at about the same rate as the text block.

Once access to the collection is gained, the external appearance of each volume and group of volumes is a useful indication of the degree of water damage. Those volumes found, usually in heaps, in the aisles will naturally be the most damaged. Not only will they have sustained the shock of falling, as rapid swelling caused them to burst from the shelves, but they will also have been exposed to water for a longer period than the volumes on the shelves above them. These will need special, flat packing and the most extensive restoration. The appearance of such volumes can be a devastating, emotional experience, but one must not panic since every volume worth the cost of salvage and restora tion can be saved.

Above the floor levels there will be distinct signs among the shelves of the locations of the wettest material. Shelves which have expanded under the pressure of swollen paper and bindings will usually contain a mixture of evenly wet as well as unevenly wet material. The proportion of evenly wet material in these situations is usually less than those that are unevenly wet. This is because books, originally shelved closely packed together, will not easily be completely saturated especially if the paper is slow to absorb. This is the major reason why so many books become misshapen and distorted after water damage and also after they have been frozen and dried. If paper is unevenly wet, it will not dry without distortion. Misshapen volumes with concave spines and convex fore-edges can be immediately identified as belonging to the category of very wet. Others that have severely swollen text blocks but that still retain some spine and fore-edge shape may indicate that they were previously bound with library binding oversewing techniques and may have sustained irreversible sewing structure damage. Others may be relatively sound in shape and these stand the best chance of drying with the minimum of distortion. Ibid.

Access

Where water damage has resulted from fire-fighting measures, cooperation with the fire marshal, and health and safety officials is vital for a realistic appraisal of the feasibility of a safe salvage effort. Fire officers and safety personnel will decide when a damaged building is safe to enter. In some cases, areas involved in a fire may require a week or longer before they are cool and safe enough to enter. Other areas may be under investigation when arson is suspected. There may be parts of a collection that can be identified early in the salvage planning effort as being especially vulnerable to destruction unless they receive attention within a few hours after the fire has abated. If the fire marshal appreciates such needs, he may be able to provide means of special access to these areas even when other parts of the building remain hazardous.

Perhaps the most important and difficult decision to make after an assessment of damage has been made, is whether to remove the wettest materials first or to concentrate on those that are only partially wet or damp. If the majority is in the latter category the best course may be to recover these items first; they may develop mold if they are left in dank and humid conditions while the wettest material is removed. A balance must be struck between the moisture reduction of the affected areas and the time involved for the safe removal of the majority of the collections in the best condition. To remove the wettest material first will obviously lower the moisture content, but it is often the case that this can be difficult and time consuming owing to the fact that shelves will become jammed with swollen wet books and boxes that may require special equipment to free them. The aim is always to recover the majority of the collection in the best condition to avoid additional harm and costs brought about by post-disaster environmental damage.

Once all entrances and aisles have been cleared, in addition to the above considerations, the most important collections, including rare materials and those of permanent research value, should be given priority unless other material would be more severely damaged by prolonged exposure to water. Examples of the latter are books printed on paper of types widely produced between 1880 and 1946, now brittle or semi-brittle. However, materials in this category which can be replaced should be left until last. Ibid.

Stabilizing the Environment

Salvage operations must be planned so that the environment of water damaged areas can be stabilized and controlled both before and during the removal of the materials. In warm, humid weather, mold growth may be expected to appear in a water-damaged area within 48 hours. In any weather, mold can be expected to appear within 48 hours in poorly ventilated areas made warm and humid by recent fire in adjacent parts of the building. For this reason, every effort should be made to reduce high humidity and temperatures, and to vent the areas as soon as the water has receded or been pumped out. Water-soaked materials must be kept as cool as possible by every means available and be provided with good air circulation until they can be stabilized. To leave such materials more than 48 hours in temperatures above 70 degrees Fahrenheit and a relative humidity above 60 percent without good air circulation will almost certainly result in heavy mold growth and lead to high recovery and restoration costs.

Damaged most by these conditions are volumes printed on coated stock and such highly proteinaceous materials as leather and vellum bindings. Starch-impregnated cloths, glues, adhesives, and starch pastes are affected to a somewhat lesser degree. As long as books are tightly shelved, mold may develop only on the outer edges of the bindings. Thus no attempt should be made, in these conditions, to separate books and fan them open.

As a general rule, damp books located in warm and humid areas without ventilation will be subject to rapid mold growth. As they begin to dry, both the bindings and the edges of books will be quickly attacked by mold. Archival files which have not been disturbed will not be attacked so quickly by mold. A different problem exists for damp books printed on coated stock; if they are allowed to dry out in this condition, the leaves will quickly fuse permanently together. Ibid.

Assessment of Damage and Planning for Salvage

Weather is often the critical factor in determining what course of action to take after any flood or fire in which archive and library materials are damaged. When it is hot and humid, salvage must be initiated with a minimum of delay to prevent or control the growth of mold. When the weather is cold, more time may be taken to plan salvage operations and experiment with various reclamation procedures.

The first step is to establish the nature and degree of damage. Once an assessment of the damage has been made, firm plans and priorities for salvage can be drawn up. These plans should include a determination of the special facilities, equipment and personnel required.

Overcautious, unrealistic, or inadequate appraisals of damage can result in the loss of valuable materials as well as confusion during all phases of the recovery operation. Speed is of the utmost importance, but not at the expense of careful planning which must be aimed at carrying out the most appropriate, safe and efficient salvage procedure within the circumstances prevailing. An efficient record keeping system is a must. Inventory of call numbers, shelf location and packing box numbers will help make the task of receiving collections returned after drying so that their original shelf locations can be identified, as efficient as possible.

Maintaining a detailed photographic and written record of all stages in the recovery operation is an essential, but often overlooked task which will aid the process of insurance claims and demonstrate the condition of the material before it is frozen and dried. We have found that on receiving materials back from a drying process, some administrators are shocked by the appearance of distorted material, believing perhaps that the condition should be much better, or be somewhat restored! The photographic record can be a very helpful reminder that distortion is mostly the result of the initial water damage and not necessarily the result of the drying process. The photographic record should provide key evidence for the reasons and nature of additional damage resulting from any part of the recovery process. Ibid.

Primary Considerations for Recovery of Water-Damaged Collections

·	Seek the advice of specialists who can assist at the site of the disaster.

·	Organize a disaster team and prepare a comprehensive plan of action, as well as plans for different contingencies.

·	Do not attempt to remove materials from the area until an overall plan with a schedule of priorities has been established and all personnel thoroughly briefed and trained.

·	In winter, turn off all heat in the building. In summer, reduce temperatures as much as possible through air-conditioning.

·	Create maximum airflow through all affected areas by opening doors and windows. If electrical facilities are operational, use as many fans as can be acquired to create a current of air so directed as to expel humid air from the building. Use dehumidifiers together with air conditioning and a good airflow. The objective is to avoid pockets of stagnant air and to reduce moisture content.

·	If house electricity is not available, hire portable generators to provide electricity for lights, fan, dehumidifiers, and other electrical services. For safety purposes, all electrical lines should be waterproofed and grounded and be administered by health and safety personnel.

·	Do not permit anyone to open wet books; to separate single sheets; to remove covers when materials are water-soaked; or to disturb wet file boxes, prints, drawings, and photographs. Such handling can result in extensive and often irreparable damage to materials that otherwise might be salvaged. Reducing the cost of future restoration must be one of the top priorities of the salvage operation.

·	Canvass the community to locate freezing and storage space.

·	Locate sources of one cubic foot milk crates and corrugated board boxes. Ibid.

Preliminary Steps in the Evacuating Water-Damaged Areas

If the materials are to be frozen, prior arrangements should have been made to ship the packed materials immediately to freezing facilities. Packed materials must not be allowed to remain on or near the site for more than a few hours, since such delay will further increase the possibility of mold development. Before actual removal of the water-soaked material begins, lighting, fans, dehumidifiers, and all possible venting should be fully operational. All work surfaces should be covered with polyethylene sheeting. Areas selected for packing or drying should be prepared for the operation by emptying them of all unnecessary equipment and furniture. Ibid.

Removal and Packing of Water-Damaged Materials -- The Work Force

Safety of the materials and future restoration costs will depend largely on the competence and dedication of the salvage crews. The work will be arduous, dirty, and often frustrating. Team leaders should not hesitate to dismiss careless and thoughtless workers. Experience has shown that well-disciplined crews having brief rest periods with refreshments about every hour and a half are the most efficient. Working salvage crews to exhaustion pays no dividends. Ibid.

Removal from Water-Damaged Area -- The Catalog and Other Records of the Collection

High priority should be given to salvaging the catalog and other records of the collection. Salvage operations should avoid any action that might remove or deface identifying marks and labels.

During the pre-recovery planning stage a decision needs to be made on whether or not to use a location number identification system which could be used after the material is returned from the drying operation to reassemble the collection in similar shelf order. There will be a need to identify and segregate materials which are very wet from partially wet; mold contaminated from uncontaminated; rare and sensitive items from the less rare and sensitive etc. If an orderly, efficient and safe recovery is to be achieved, together with a control over the choice of drying and other special measures needed to save rare and sensitive materials, a box coding system is indispensable.

At least one person should be assigned specific responsibility for making an inventory at each location where the materials are taken from the shelves and boxed. This person might also be given charge of supervising the boxing and box coding process.

Conveyor belts and human chains are normally used to remove large numbers of material from each shelf, pack them in corrugated boxes or plastic milk crates and to move them to the loading site for shipment to cold storage facilities. It is at this time that a great deal of additional damage and confusion can occur. The number of people involved in this operation and their behavior needs to be closely supervised. Try to initiate a rhythm when using human chains that keeps everyone busy without being over taxed. Too many helpers will hamper progress, encourage loafing and generally reduce the efficiency of the operation. It is highly desirable to instruct the team daily on the tasks to be carried out and to keep them informed as to the major objectives of the recovery operation and as to any changes that have been made to the master plan.

An efficient and dedicated work force needs to be provided with all the accouterments of human survival, such as regular rest periods, a place to eat, a convenience to wash and clean up and immediate access to medical attention.

Manuscripts and other materials in single sheets create particularly difficult problems if they have been scattered. An indication of the approximate location in which they are found during the salvage operation may be extremely helpful at a later date. Materials should never be moved from the site in large batches or left piled on top of each other, either at the site or in adjacent temporary housing, since the excessive weight of water-affected books and paper records can lead to severe physical damage.

When flood-damaged books were removed from the Biblioteca Nazionale in Florence following the river flood disaster of 1966 substantial numbers were piled high outside the library building while awaiting shipment to drying facilities. This action caused significant damage to the books from the weight of water-saturated volumes and lead to very high costs of post-disaster restoration. Ibid.

Removal and Packing

The aisles between stacks and main passageways will probably be strewn with sodden materials. These must be removed first, separately, by human chain, in the exact condition in which they are found. Open books will be greatly swollen, but no attempt should be made to close them. Closing them will cause further damage by tearing the leaves, since paper will not slide when wet. Instead, books should be passed undisturbed to an adjacent dry area where an awaiting team may pack them without disturbing their shape. This particular type of material must not be packed tightly but should be packed flat in boxes and separated with at least one layer of freezer paper and one sheet of 1/2" polystyrene between each open book.

The packing team should have approximately the same number of people as the team that passes the damaged material to them. This will avoid bottlenecks and stacking materials on the floor awaiting packing. If a sufficient number of people and conveyor belts are available, the most efficient place to pack damaged materials will be on site. Teams will have to be organized to assemble packing materials and supply them to the packers in a smooth flow. Use of a second human chain or conveyor will reduce bottlenecks and the likelihood of incoming supplies interfering with the flow of packed materials being passed out of the building. After the aisles have been completely cleared, the main work of recovery can begin. Hopefully, a decision will have been made as to which material to remove first: the wettest or the ones in the best condition. As stated earlier, if the majority is only damp and in relatively sound condition, these could be removed first and more rapidly than other materials. In these circumstances de-shelving and packing will be a relatively quick operation and will help to establish a smooth worker flow. As each line of shelves is emptied, an assistant should code each box and record the box number and its general contents in a notebook. The contents of archival storage boxes are unlikely to be saturated with water if they were previously positioned close together. However, since certain types of boxes have a corrugated inside layer, they may be very wet, even though the major portion of the contents is only damp. In such cases, it is best to repack the contents in new boxes or in plastic milk crates. This will not only make each unit lighter to lift and prevent the collapse of a wet box but will also speed the drying process. When repacking, it is important that the new boxes be properly identified. Ibid.

Disposition of Remaining Materials and Cleaning of Water Exposed Areas

If the wettest materials were removed first the drier material will usually be above the first four or five shelves and packed closely together. On no account should this third category be separated or spaced out during the earlier salvage efforts. Closely packed materials will not readily develop mold internally.

However, since these will have been in a very humid atmosphere for, maybe several days, it is likely that some mold will have developed on the outer edges of bindings and boxes. This is less likely to occur if, during the evacuation of the wettest materials, every effort had been made to reduce temperatures and humidity levels and establish a good airflow.

There may be books and box files in such good condition that they need not be sent to freezing facilities but can be dried in ambient conditions. On no account however should the drying be attempted in the location in which they were found because the environment will be totally unsuitable. They should instead be removed to a controlled environment while shelves, wall, floors, and ceilings are sterilized and necessary maintenance work is being done to return the site to its normal condition. If moved, materials should be stacked with air spaces between them provided that the drying area has a good circulation of air, together with air-conditioning and dehumidification. If air-conditioning is not available, fans and dehumidifiers should be used to keep air moving and to extract moisture from the area. The relative humidity of a drying area is no guide to the actual moisture content of cellulose materials. The normal water content of paper is between 5 and 7 percent by weight. Materials which feel relatively dry to the touch as they come out of a humid, flood-damaged area, may actually contain moisture from above 10 to 20 percent.

Heat is one of the best means of drying, but since it increases the risk of mold development on humid books and documents, it should be used only if a good circulation of air and dehumidification can be established. Hydrothermographs for recording temperature and relative humidity should be installed to monitor the general area, and moisture-content meters used to measure the moisture in the materials themselves. Ibid.

Cleaning After a River Flood

The safest time to clean materials is after they have been dried. If water-damage is the result of a river flood then the following might, under certain circumstances, be considered. The Florence experience demonstrated that the best time to remove mud was after the books were dry. However some books did benefit from partial cleaning in the wet state.

If adequate assistance is available, mud deposits on books which will not be further damaged by water may be washed off in clean, running water. Closed books may be held, one at a time, under water and the excess mud removed with a hose connected to a fine spray head. Similar washing should not be attempted with opened volumes, manuscripts, art on paper, or photographs.

Rubbing and brushing should be avoided, and no effort be made to remove oil stains. Anything which is hard to remove is better left until after drying, when techniques for removal can be worked out during the restoration stage. In some cases, printed books bound in cloth or paper can be left immersed in clean running water for as long as two weeks. Although this should be avoided if possible, it is preferable when the only alternative is leaving such books in warm, humid air while awaiting attention. Ibid.

Thorough Washing to Remove Heavy Deposits of Mud

A more thorough washing procedure, intended to remove as much mud and slime as possible from books, requires six to eight tanks big enough to accommodate the largest volumes in the collection. This process is obviously wet and messy and needs to be set up outdoors in fair weather or in an area fitted out to use and remove large quantities of water. Since large quantities of water are required, the area will be wet and dirty throughout the operation, and good drainage is therefore essential.

Any rustproof receptacles may be used if they are large enough, but plastic garbage cans (20 or 30 gallons) are recommended. Each can should be equipped with a hose to provide low-pressure, continuous water flow to the bottom so that dirty water, as it overflows the rim, will be constantly replaced by fresh. Each hose should be fastened securely to prevent damage to the books being washed. Wooden duck-boards, rubber boots, gloves and aprons are recommended for the protection of workers.

Keeping a book tightly closed, a worker should immerse one book at a time in the first can and remove as much mud as possible by gentle agitation under the water. Workers should not use brushes and or any tool which would cause an aggressive rubbing action. Books should be passed from one can to the next and the same operations repeated until most of the mud has been removed. At the last can, books should be rinsed by spraying them gently with a fine stream of water. No effort should be made to remove mud which continues to cling after sponging under water. This is much better done when the books are dry.

Finally, excess water can be squeezed from books with hands pressure; mechanical presses should never be used. It must be emphasized that the above procedure should be attempted only by a carefully instructed team and in a properly fitted-out area. If there is any doubt about the ability of the team to follow directions, washing should not be attempted. There are many classes of books which should not be washed under any circumstances, and it is therefore imperative to have the advice of an experienced book conservator who can recognize such materials and who understands their treatment requirements. Ibid.

Principles of Stabilization by Freezing

The most generally accepted method of stabilizing water-damaged library and archival materials before they are dried is by freezing and storing at low temperatures. This buys time in which to plan and organize the steps needed to dry the material and to prepare a rehabilitation site and the building for return of the collections after drying. Freezing provides the means for storing water damaged material safely and for an indefinite period of time in similar physical condition in which they were found, preventing further deterioration by water and mold while awaiting treatment.

Freezing is not a drying method, nor can it be expected to kill mold spores, but it is highly effective in controlling mold growth by inducing a dormant state in the spores. If mold damaged material is frozen it is important that the drying method chosen must prevent mold spore activity during the drying process. For this reason it is important to segregate such material during removal and packing operations.

Stabilization by freezing also provides important advantages when it is not possible to immediately assess the value of the damaged materials or to determine which items can or cannot be replaced. In other words, stabilization gives time in which to estimate recovery costs, to prepare adequate environmental storage conditions, and to restore the building. In some cases, it may be necessary to restore or rebuild the original facilities - a process which can require a long period of time.

Had freezing techniques been used after the catastrophic Florence flood in 1966, thousands of additional volumes could have been saved completely or would have suffered significantly less damage. The Florentine libraries which sustained the greatest losses contained mostly 19th and 20th-century materials. In these collections, losses were heaviest among books printed on coated stock, whose leaves stuck together during drying and could not be separated afterward. These losses could have been largely prevented if the materials had been frozen while wet, and if drying methods now known had been used to prevent adhesion of the leaves.

The effect upon freezing water soaked volumes which have lost their shape or have had their binding structures damaged by immersion, will be to slightly increase the thickness of volumes by the physical action of ice crystals, but this additional increase in thickness has been found to contribute no significant problems to already damaged books. Studies conducted by the Research and Testing Office of the Library of Congress have uncovered no evidence of any damage to cellulosic and proteinaceous materials caused solely by the action of freezing.

Freezing as a salvage method has other advantages. It can stabilize water-soluble materials such as inks, dyes, and water stains etc. which would otherwise spread by wicking action if they were dried from the wet state by conventional drying methods. Freezing provides the means by which water-soluble compounds will remain stable during a freeze-drying process which involves the removal of water by sublimation. This is the only known drying method capable of drying without further spreading of water soluble compounds, provided that the frozen state of the material is maintained before and throughout the drying process. Ibid.

Cold Temperature Storage Conditions

The size and formation of ice crystals is governed by the rate and temperature of freezing. Blast-

freezing used for certain types of food-stuffs is designed to freeze in a few hours, often having

temperatures lower than -50 degrees Celsius. The advantage of quick freezing is in keeping

ice crystals very small, resulting in a limited amount of swelling. The availability of blast-freezing facilities may not be possible following water damage. In normal circumstances,

the freezing process will be slower and therefore the formation of ice crystals will be larger; this should not cause problems for the majority of library and archive collections.

Once frozen, cold temperature conditions should be maintained at about 0 degrees Fahrenheit

(-18 degrees Celsius). Lower temperatures will do no harm but higher temperatures may result in an increase of the size of ice crystals. Ibid.

Preparation for Freezing

Before freezing, it may seem tempting to wash away accumulated debris-particularly if this is the result of a river flood. This is rarely advisable or safe because of lack of time, skilled workers and a pure water supply, as well as the quantity of material to be handled. (Aqueous washing to remove smoke damage should never be attempted under any circumstances.)

Washing should never be attempted by untrained persons as this will cause further damage, nor should time be taken for this purpose if so little skilled help is available that any significant delay in freezing the bulk of the materials would result. The washing of materials containing water-soluble components, such as inks, watercolors, tempera or dyes should not be attempted under any circumstances.

Experience has shown that such materials, as well as those that are fragile or delicate, can be seriously or irreparably damaged by untrained workers attempting to clean and restore on-site. Such materials need expert attention and hours of careful work if damage is to be kept to a minimum. The period of emergency action and first aid is a dangerous and unsuitable time for the careful work required to restore materials to near-original state. The general condition of the damaged material will determine how much time can be spent in preparation for freezing. At the very least, bound volumes should be wrapped with a single fold of freezer paper, or silicone paper, if it is likely that their covers will stick together during the freezing process.

All rare, intrinsically valuable and delicate material should be prepared for freezing separately from other materials and also in separate categories so that each can be located and identified before they are dried. Each category may require a different type of drying than used for the other, less-sensitive materials. For instance, early printed books and manuscripts are made up of a variety of material including vellum, leather, paper, wood, metal, ivory, inks and water color media. Others will be delicate and or highly water sensitive. These will need to be dried very carefully and if freeze-drying is used it should be undertaken with the minimum amount of internal chamber heating. If only a few items are involved it may be preferable to send them directly to a certified conservator for immediate treatment. Ibid.

Containers and Methods of Packing for Freezing

The choice of packing containers should be carefully considered. Although corrugated board boxes are cheaper to purchase, locate and store on site than plastic type milk crates, they may restrict the rate and efficiency of drying and also be prone to collapse when filled with wet material. If it is possible to decide in advance what method of drying is to be used, be guided by the technical requirements of the vendor s drying system. For instance, if freeze-drying is to be used, one cubic foot plastic milk crates might be preferred, since these provide open spaces within the interlocking crates to aid in the efficient out-gassing of ice by sublimation.

With some forms of vacuum drying where sublimation does not occur, corrugated boxes may be quite suitable, depending on the location of the heat source in the chamber. In either case, containers should not be larger than approximately one cubic foot, to avoid excessive weight, a vital consideration for workers removing material from site and also to help reduce damage from collapsing boxes. Usually boxes will be prepared for freezing on pallets and this is where the weight of heavy wet boxes can collapse and cause additional damage to material within the pile.

To avoid this, use plastic milk crates or very sturdy corrugated boxes for the wettest material and re-box file records if their original boxes are saturated with water. Endeavor to use one size and type of box. If this not possible, do not mix sizes when packing on pallets. The number of boxes per pallet should be no more than can be supported without collapse.

Although faster freezing and drying will result if boxes are not packed tightly, the contents will distort during the drying operation. To achieve the best drying results for books, they should be packed closely together so that drying is done under some restraining pressure. A book should never be packed foredge down as the weight of the text block will cause an inversion of its natural round shape. Pack books spine-down or flat and avoid placing larger volumes on top of smaller ones to avoid sagging which will be costly to correct during restoration.

The decisions taken at this stage will greatly affect the outcome and costs of the processes used for cold storage, drying and restoration. It has, unfortunately, not been sufficiently appreciated in the past that care in packing at this stage will significantly reduce post-recovery costs.

High costs certainly occur if boxes are stacked on pallets in mixed sizes which will increase the potential for collapse under the weight of water, crushing and damaging the material in the process.

It should be possible to move the wet materials directly from library to freezing facility, preferably in refrigerated trucks which can be drawn up to the loading site. For small collections of books and documents, dry ice may be used to freeze the material for transport in un-refrigerated trucks to long-term freezing facilities. (Gloves should be worn at all times when handling dry ice). Ibid.

THE PACK OUT

Each wrapping/boxing team requires four people: 1 to set up the flattened boxes, 2 to wrap the books and 1 to box.  If the freezer wrap has not been pre-cut, one or more people will be needed to cut strips of paper from the rolls.

Freezer paper can be wrapped around individual volumes, slick side toward the book, to prevent bleeding of dyes and adhesives.  Wrap only if the scope of the disaster allows sufficient time to do so.  It is more important, however, to get the damaged materials packed and to the freezing facility than it is to wrap each volume.

Books should be boxed spine down, one layer deep, to minimize damage to binding.  Large volumes can be laid flat.  Pack books of the same size next to each other to minimize warpage.  File folders are best packed vertically.  Do not attempt to remove mud or to open books.  Boxes should not be packed tightly; swelling will continue after the boxes are packed.

Place lids on boxes and label each end with the appropriate LC classification letters.  Remove boxes to end of ranges and stack no more than four boxes high.  Box collectors with hand trucks and dollies will transfer the stacked boxes to the evacuation site where they will be shrink-wrapped on pallets to minimize transit damage and reduce handling costs.  Pallets will be loaded by forklift onto trucks and transported to the freezing facility.

A count of the number of boxes shipped should be recorded at the evacuation site. University of California at Davis Disaster Prevention, Preparedness and Recovery Plan [Web page]

Vacuum and Freeze Drying Technologies

It is important to understand that the processes used by vacuum and freeze-drying companies differ considerably depending on the specific requirements of the material to be dried. The majority of these companies have developed their technologies for food. Few have had experience in drying paper and books and therefore may not know if their normal operating system would be safe, or cost effective for this purpose. Freeze-drying has a number of significant advantages over vacuum drying since water remains in the frozen state during sublimation, a process which removes water from the solid state to the gaseous state. This avoids most of the problems associated with expansion, sticking and wicking of water sensitive and soluble media. Vacuum drying, generally considered to be a process that changes a liquid to a vapor, will result in a much greater risk of expansion, distortion, sticking, and staining.

Although both drying methods have been found to produce satisfactory results in a number of disaster recovery events, comparison between the two following a disaster has not been made. Our preference is for freeze-drying because it is the less aggressive of the two methods. However, there are situations where for instance, archival documents have been affected and where there is a low percentage of intrinsically valuable material, where vacuum drying has provided satisfactory results. The choice between the two should be governed by the nature, value and condition of the damaged material. Rare collections of significant value need to be dried with due regard to the sensitivity of the substrate and media and it is for this reason why we suggested earlier that such materials be segregated from the less rare.

Freeze-drying which is used to dry animal specimens, does so at very low internal chamber temperatures, lower than is used for most food processes. One animal specimen may take several weeks to dry. At this slow rate of drying the costs are high. Most paper and book material can withstand higher temperatures than those used to dry delicate animal specimens and there is a need for thermal energy to make the process efficient and cost effective.

If a vacuum or freeze-drying chamber is designed to operate with internal chamber heat sources, these must not touch the material to be dried, to avoid over heating and scorching. The internal temperature of a chamber should be no greater than 100 degrees Fahrenheit (37.8 degrees Celsius). For sensitive materials, including early book material where there is a mix of paper, vellum, leather and wood etc., below ambient temperatures or those used to dry animal specimens should be used, to dry the material slowly and under carefully monitored conditions.  (Note: In specifying an upper limit of 100 degrees Fahrenheit we consider this to be a safe temperature. There is insufficient data at this time to evaluate the effects of higher temperatures).

It is important to realize that the success of any large drying system depends on the ability of the system to stop the development of mold during and after the drying process. Be aware of the risks in accepting material returned from commercial drying processes unless there is a guarantee that none will be returned damp or wet. If mold develops after return, it may not be possible to detect it, if the material remains boxed. If care was taken to segregate mold-contaminated from non-contaminated items during recovery, boxing and freezing, this will help determine if the drying was carried out properly. If mold develops in the non-contaminated material, the chances are that either the drying was not done correctly or that drying was not complete.

Mold-infected material, if dried completely under freeze-drying conditions, can be safely controlled for a short period of time, so that the spores remain quite dormant if stored after drying in an air conditioned environment maintained at 50 to 55 degrees Fahrenheit and a relative humidity of 35 percent or lower. However they must not be returned to the library or archive shelves until the mold contamination has been treated. For this reason we recommend that at the end of the drying cycle and while still in the drying chamber all mold-contaminated material be sterilized. If extreme care was not taken to separate contaminated from non-contaminated materials before the drying operation, we recommend that each drying load be sterilized. National Park Service. Disaster Plan. [Web page].

Rehabilitation After Drying

If maximum benefits are to be gained from stabilization by freezing, every effort should be made, first, to identify and assess the value, condition, and total numbers and types of materials damaged, and second, to draw up comprehensive lists of those materials which can be replaced and those which should be reclaimed and restored. Replacement is nearly always cheaper than restoration. Volumes to be reclaimed will need to be evaluated in terms of the amount of restoration needed and probable costs. The best time to make such judgments, if a disaster preparedness plan does not exist, is after the volumes have been dried and before they are returned to the library or archive shelves

The following represent basic steps that need to be taken after drying in order to begin returning the material to normal housing environments.

Unless a drying company can guarantee in writing that no material will be returned boxed if it has a water content exceeding 7% by weight, there is a high possibility that some boxes will contain damp material that will add to the risks of post drying mold development, and which, if allowed to develop, will quickly spread to other uncontaminated material, if left unchecked and therefore undetected.

It is important when preparing specification for a drying contract that acceptable water content is not specified as an average of a book’s total water content. For instance the text block of a book may be measured at far less than 7% but the water content of the book cover boards may contain higher than 7% of water. Therefore it is necessary to specify that the waters content of all the books composite materials be less than 7%.

Do not store the material in unopened boxes immediately upon return from the drying facilities, even if this seems to be the most convenient action to take.

All books and paper file records should be unboxed and placed on open shelving in a well ventilated, air-conditioned rehabilitation area, well separated from the main collections. The rehabilitation area makes it easier to assess the condition of the dried materials, as well as to identify those that can be replaced and those that must be cleaned and restored.

A carefully organized, random inspection of mold- infected materials should be conducted daily by personnel trained to carry out this important task.

Whether materials have or have not been sterilized during the drying process, it is necessary to monitor their behavior as a check against the effectiveness of drying and sterilization and to identify any potential for mold growth and to take the appropriate action, before the return of these materials to the main collections.

We are concerned here with monitoring the dried volumes while they are in the rehabilitation area, and after their return to the main stacks. This monitoring should be continued at regular intervals for at least a year after they are returned to the main library shelving.

In preparing the rehabilitation area, provide about twice the number of shelves as would be needed for normal book requirements. This will compensate for the effects of distorted and expanded books and provide sufficient air space to allow the material to regain their moisture equilibrium content which, depending upon circumstances, may take a week or two.

Theoretically, equilibrium moisture regain can be accomplished at the end of a drying run while the material is contained in the drying chamber. The chamber can be back filled with moisture to achieve the desired result. However this is only possible and safe if the drying method has been guaranteed to dry the material completely. If there remains some partially damp material at the end of a drying run, back filling the chamber with moisture would make such material more vulnerable to mold growth.

The rehabilitation area should be maintained at a relative humidity of 30 to 40 percent and a temperature of less than 65º Fahrenheit. Both humidity and temperature controls must be adjustable.

It is desirable to maintain the collection in the rehabilitation area for a period of at least six months. At this time, temperature and humidity in the rehabilitation area can be gradually changed to duplicate conditions in the stack areas to which they will be returned. At the end of this time, if no mold growth has occurred, the volumes can be returned to the main stacks and monitored as indicated above. It is highly desirable but usually not practical to leave volumes in the rehabilitation area for an added six months in an environment that duplicates normal stack conditions, as a check against post drying mold growth.

No materials should be returned to the main library shelves without very careful inspection, and preferably not before all necessary cleaning and restoration has been completed. Ibid.

Evaluation of Loss

When a flood or fire-damaged collection is covered by insurance, full settlement of a claim cannot be realized until the lost and damaged materials have been listed and their values established. The extent and success of possible restoration must also be determined. In the event that a claim is anticipated as a result of such damage, every item should be salvaged, frozen, and dried. After drying, the affected materials should be shelved in a specially equipped environmental storage area, isolated from the main stacks, and there inspected and monitored over a period of time. Such a policy is the best guarantee of sound judgments by custodians, consultants, and adjusters when they must calculate the degree of loss as a basis for compensation. Ibid.

Summary of Emergency Procedures

·	Seek the advice of book and paper conservators with experience in salvaging water-damaged materials as soon as possible.

·	Turn off heat and create free circulation of air.

·	Keep fans and air-conditioning on day and night and the use dehumidifier, insuring a constant flow of air is necessary to reduce the threat of mold.

·	Brief each worker carefully before salvage operations begin, giving full information on the dangers of proceeding except as directed. Emphasize the seriousness of timing and the priorities and aims of the whole operation. Instruct workers on means of recognizing manuscripts, materials with water-soluble components, leather and vellum bindings, materials printed on coated paper stock, and photographic materials.

·	Do not allow workers to attempt restoration of any items on site. This was a common error in the first 10 days after the Florence flood, when rare and valuable leather and vellum-bound volumes were subjected to scrubbing and processing to remove mud. This resulted in driving mud into the interstices of leather, vellum, cloth, and paper, caused extensive damage to the volumes, and made the later work of restoration more difficult, time consuming, and extremely costly.)

·	Carry out all cleaning operations, whether outside the building or in controlled environment rooms, by washing gently with fresh, cold running water and soft cellulose sponges to aid in the release of mud and filth. Use sponges in a dabbing motion; do not rub. These instructions do not apply to materials with water-soluble components. Such materials should be frozen as quickly as possible.

·	Do not attempt to open a wet book. (Wet paper is very weak and will tear at a touch. One tear costs at least one dollar to mend!) Hold a book firmly closed when cleaned, especially when washing or sponging. A closed book is highly resistant to impregnation and damage.

·	Do not attempt to remove mud by sponging. Mud is best removed from clothes when dry; this is also true of library materials.

·	Do not remove covers from books, as they will help to support the books during drying. When partially dry, books may be hung over nylon lines to finish drying. Do not hang books from lines while they are very wet because the weight will cause damage to the inside folds of the sections.

·	Do not press books and documents when they are water soaked. This can force mud into the paper and subject the materials to stresses which will damage their structures.

·	Use soft pencils for making notes on slips of paper but do not attempt to write on wet paper or other artifacts.

·	Clean, white blotter paper, white paper towels, strong toilet paper, and unprinted newsprint may be used for interleaving in the drying process. When nothing better is available, all but the color sections of printed newspapers may be used. Care must be taken to avoid rubbing the inked surface of the newspaper over the material being dried; otherwise some offsetting of the ink may occur.

·	Under no circumstances should newly dried materials be packed in boxes and left without attention for more than a few days.

·	Do not use bleaches, detergents, water-soluble fungicides, wire staples, paper or bulldog clips, adhesive tape, or adhesives of any kind. Never use felt-tipped fiber or ballpoint pens or any marking device on wet paper.

·	Never use colored blotting paper or colored paper of any kind to dry books and other documents.

·	Used and damp interleaving sheets should not be reused.

·	Frequent changing of interleaving material is much more effective than allowing large numbers of sheets to remain in place for extended periods.

·	Newsprint should not be left in books after drying is complete.

·	A good grade of paper toweling is more effective than newsprint, but the cost is much greater. Ibid.

For Further Reading

Hendriks, Klaus B. and Brian Lesser.  1983.  “Disaster Preparedness and Recovery:  Photographic Materials.”  In American Archivist.  Winter:  52-68.

Northeast Document Conservation Center.  1994.  Emergency Salvage of Photographs.  Technical Leaflet, Technical Management.  Andover, MA:  NEDCC.

Waters, Peter.  1975.  Procedures for Salvage of Water-Damaged Library Materials.  Washington, DC:  Library of Congress.

National Park Service Disaster Plan online at http://www.cr.nps.gov/museum/publications/primer/primintro.html.

Water Damage Recovery Procedures Chart From “Salvage Operations for Water Damaged Collections” by Betty Walsh, Western Association for Art Conservation Newsletter.  Vol. 10, No.2

| Material | Priority Action | Handling Precautions | Packing Method | Drying Method |
| --- | --- | --- | --- | --- |
| PAPER |  |  |  |  |
| Manuscripts, documents, small drawings | Freeze or dry within 48 hours | Do not separate single sheets | Interleave between folders; pack in milk crates or cartons | Air, vacuum, or freeze dry |
| Watercolors, other soluble material | Immediately freeze or dry | Do not blot |  |  |
| Maps, oversized prints, manuscripts | Freeze or dry | Do not separate single sheets | Pack in map drawers, bead trays, flat boxes or ply covered plywood | Air, vacuum or freeze dry |
| Coated papers | Immediately pack, then freeze or dry within 48 hours |  | Keep wet in containers lined with garbage bags | Freeze dry only |
| Framed prints and drawings | Freeze or dry within 48 hours |  | Unframe if possible, then pack as for manuscripts or maps above | Once unframed and unmatted, air or freeze dry |
| BOOKS |  |  |  |  |
| Books and pamphlets | Freeze or dry within 48 hours | Do not open or close, do not separate covers | Separate with freezer paper, pack spine down in milk crate or cardboard box | Air, vacuum or freeze dry |
| Leather and vellum bindings | Immediately freeze | Do not open or close, do not separate covers | Separate with freezer paper, pack spine down in milk crate or cardboard box | Air or freeze dry |
| Books and periodicals with coated papers |  | Do not open or close, do not separate covers | Keep wet; pack spine down in containers lined with garbage bags | Freeze dry only |
| PAINTINGS | Immediately dry | Drain and carry horizontally | Face up without touching paint | Air dry |
| FLOPPY DISKETTES | Immediately pack | Do not touch diskette with bare hands | Contact supplier for best method | Contact supplier for best method |
| Material | Priority Action | Handling Precautions | Packing Method | Drying Method |
| SOUND & VIDEO RECORDINGS |  |  |  |  |
| Discs-CD, DVD | Dry within 48 hours. Freezing is untested; if necessary freeze at above 0° F (-18° C) | Hold discs by their edges | Pack vertically in ethafoam-padded plastic crates | Air dry |
| Sound and videotapes, including U-Matic tapes | Freezing is untested. If necessary, freeze at above 10° F |  | Pack vertically into plastic crates or cardboard cartons. Do not put any heavy weight on the sides of reels or cassettes | Air dry |
| PHOTOGRAPHS |  |  |  |  |
| Wet Collodion photographs (ambrotypes, tintypes, pannotypes, negatives) | Recovery rate is low. Immediately dry. | Handle with care - glass supports or glazing | Pack horizontally in padded container | Air dry face up. Never freeze. |
| Daguerreotypes | Immediately dry | Handle with care - usually cased behind glass | Pack horizontally in padded container | Air dry, face up |
| Nitrates with soluble emulsions | Immediately freeze | Do not blot |  | Air dry; test freeze drying |
| Prints, negatives, and transparencies | Freeze or dry within 72 hours. Salvage order: 1)color photographs; 2)prints, transparencies | Do not touch emulsions with bare hands | Keep in cold water. Pack in containers lined with garbage bags. | Order preference: 1)air dry; 2) thaw and air dry; 3) freeze dry. Do not vacuum dry. |
| Motion pictures | Rewash and dry within 72 hours | Do not remove from boxes; hold cartons together with rubber bands | Fill film cans with cold water and pack in plastic bags or cardboard cartons lined with garbage bags | Arrange for film processor to rewash and dry |
| Microfilm rolls | Rewash and dry within 72 hours |  | Fill boxes with water and pack in boxes of 5 per box; line box with garbage bags | Arrange for a microfilm processor to rewash and dry |
| Aperture cards | Freeze or dry within 48 hours |  | Keep wet inside a container lined with garbage bags | Air dry |
| Jacketed microfilm | Freeze or dry within 72 hours |  | Keep wet inside a container lined with garbage bags | Air dry |

Infestation

Prevention Activities

Insects and rodents are most commonly encountered in warm, damp environments with poor light.  To discourage these pests, temperature and relative humidity should be kept low.  Because of its ability to attract insects and rodents, food should be kept out of public areas. Food and food waste in employee break rooms should be disposed of in air-tight trash receptacles to limit pest attraction.  Windows, doors and vents should remain closed as much as possible in order to hinder their access to the building.  Vegetation should be kept at least 18 inches from the exterior of the building and all new acquisitions entering the building should be checked for infestation.

Emergency Procedures

If droppings or other evidence of infestation is encountered, staff should first determine the type of pest in question and then determine if the problem can be taken care of in house or if an exterminator needs to be consulted.  Infested items and those closest to them should be separated from the rest of the collection to undergo treatment.

If you find a situation which may indicate the presence of active insects or other pests such as rodents:

·	Assess the situation.

·	What type of infestation is it?

·	Is it a small or large infestation?

·	Is collection material being affected?

·	Page Security (802-7022) and submit Facilities Services Request

·	When contact has been made, commence short term response actions for insect and vermin infestation   From National Library of Australia NLA collection Disaster Plan [Web page]. http://www.nla.gov.au/policy/disaster/  [Accessed February 24, 2004].

Recovery Procedures

Several options for pest extermination are available.  See “For Further Reading” below to determine the best course of action. After the pests have been removed, a careful cleanup of all remains is essential.  The remains of insects only serve as an attraction for future infestations.  Materials that have been treated should only be reunited with the collection after the determination that all pests have been eliminated.  Damaged materials should be evaluated for possible conservation procedures or replacement.

Short Term Response Actions

·	Assess the infestation in consultation with an outside conservation consultant

·	If necessary, arrange for samples to be referred to outside agencies for identification

·	Arrange for a thorough inspection of adjacent areas and an inspection of the rest of the building to identify other affected areas

·	Coordinate pest control procedures in the affected area

If collection material has been affected:

·	Assess the material

·	Coordinate an appropriate treatment response in consultation with collection managers

·	Ensure records of all material movements are maintained at all times

When the situation is stabilized:

·	Commence long term recovery actions for insect and vermin infestation

Long Term Recovery Actions

Collection managers will:

·	Supervise appropriate pest control procedures, carried out by the Library's pest control contractor

·	Arrange for close monitoring of the area for signs of re-infestation

·	Process collection material prioritized for fumigation and/or repair

·	Package and send material that cannot be adequately fumigated in-house to an outside fumigation company

·	Return fumigated, treated and checked material to the collections

·	Process collection material identified for replacement or discard

The Collections Disaster Coordinator conducts a post disaster assessment to:

·	Analyze the successful and failing aspects of the immediate, short and long term actions taken

·	Prepare a written report on the incident

·	Propose changes to integrated pest management procedures if necessary

·	Make changes to the disaster plan where necessary Ibid.

For Further Reading

Harmon, James D.  1993.  Integrated Pest Management in Museum, Library, and Archival Facilities.  Indianapolis:  Harmon Preservation Pest Management

Olkowski, William, Sheila Daar, and Helga Olkowski.  1991.  Common Sense Pest Control.  Newton, CT:  The Taunton Press.

Parker, T.A.  1987.  “Integrated Pest Management for Libraries.”  In Preservation of Library Materials, merrily A. Smith, ed.  From Conference held in the National Library of Austria, volume 2.  New York:  103.

Story, Keith O.  1985.  Approaches to Pest Management in Museums.  Suitland, MD:  Smithsonian Institution.

Wellheiser, Joanna G.  1992.  Nonchemical Treatment Processes for Disinfestation of Insects and Fungi in Library Collections.  Munich:  K. G. Saur.

Pest Web:  http://www.pestweb.com [accessed January 29, 2003]

Mold and Other Growths

Prevention Activities

Mold damage serves as a serious threat to the AHC due to its location in our hot and humid climate.  Because molds are always present in the air, great care must be taken in developing environmental conditions that do not promote mold spore growth and reproduction.  Temperatures and relative humidity in the institution should be kept moderately low.  For best results temperatures should remain below 70F and relative humidity below 50%.  Good air circulation and clutter-free storage areas are also important mold growth deterrents.

Prevention

The best means to prevent or control the spread of microorganism growth is to deny the spores the moisture necessary for germination. Therefore, regulating the environment, especially the RH, is essential for preventing the deterioration of a museum collection from microorganism growth.

RH levels should be routinely monitored. Spore germination is less likely to occur if RH is controlled between 45% and 55%, but RH should be kept below 65%. When RH levels rise above 65%, the use of portable dehumidifiers will be necessary to reduce the moisture content of the air. A temperature between 18 degrees C and 20 degrees C (64 degrees F to 68 degrees F) should be targeted. These levels only decrease the potential of germination and growth; they do not eliminate it. Therefore, other factors, such as adequate air circulation should be maintained; a fan will help to increase circulation.

Problem environmental conditions that may contribute to higher humidity levels need to be corrected. Repair leaking pipes, gutters and downspouts, cracked windows, a problem roof, deteriorated brick, masonry pointing, or cracked walls.

It is also important to keep any area that houses museum-type collections clean and free of dust and dirt and organic debris that can nourish spores.

Silica gel and other buffers can help adjust RH conditions within a sealed space, such as in a storage cabinet or exhibit case. These buffers will absorb or release moisture into the surrounding atmosphere. The quantity of buffering material to place within the space must be customized for each situation and a conservator should be consulted for assistance in determining this need. It takes time, experience, and careful monitoring to ensure that the buffers are performing as intended. National Park Service. Disaster Plan. [Web page].

The Microorganisms

Fungi are simple-celled organisms that do not need energy from light for growth. The fungi bear microscopic spores that are produced in enormous quantities, are always present in the air, and spread via air currents. They are often water repellant and are resistant to desiccation (drying out). Extreme cold and heat will destroy them.

When the spores are in a favorable environment, they will germinate. What constitutes a favorable environment is different for each species. After landing on a host material, a spore must obtain sufficient moisture to germinate and find enough food. Without moisture, the spores will lie dormant until favorable conditions occur.

For this reason, it is important to control the environmental conditions where museum collections are stored or exhibited. Temperatures should not exceed 24 degrees C (75 degrees F) and relative humidity  (RH) not rise above 65%. These conditions are maximum levels and only reduce the potential for microorganism growth. They do not eliminate the threat. Some microorganisms can grow in significantly lower temperatures and at lower RH levels. Certain materials need to be stored with lower RH levels to prevent growths.

NOTE: Some species of microorganisms cause health risks in the form of chronic lung irritation. Always exercise caution when handling badly infested materials, i.e. wear a high-efficiency particulate air (HEPA) filter respirator and disposable gloves. Ibid.

Susceptible Materials

Microorganisms need organic materials to supply nutrients and, therefore, museum-type objects composed of organic materials are potentially at risk. Cellulose-based materials, such as cotton, linen, paper and wood, and proteinaceous materials such as leather and hair cloth are particularly susceptible to direct attack by microorganisms.

Inhospitable materials, such as plastics, are not immune from fungal growths but how they support these growths is not fully understood by biologists. Certain mites feed on fungi and can carry spores onto normally resistant materials. As the mites die, they become the nutrients for a new fungal colony. This ability to exist on almost any material characterizes microorganisms as primary agents of deterioration. Ibid.

Damage

Microorganisms will permanently damage the materials supporting them. They will stain textiles and decrease the strength of the fabric. The scattered spots known as foxing on paper prints or drawings is damage resulting from these growths. Leather is particularly susceptible to the actions of microorganisms and will be stained and weakened by them. As a by-product, fungi can produce organic acids that will corrode and etch inorganic materials.

Emergency Procedures

Determine the cause and modify the environment.  Check the temperature and relative humidity.  If the temperature is above 75 degrees F, lower it to between 68 degrees F and 72 degrees F or lower, if possible.  If the RH is above 60%, bring it down to 50% or lower.  If the air-conditioning system merely lowers the temperature of the outside air prior to moving it through the building, turn it off because cooling the air without removing the moisture will increase the humidity.  The rate of air circulation should be increased.

Portable dehumidifiers and fans can be used during a severe outbreak, but they are only temporary measures.  If such outbreaks are a recurring problem, then the environment must be permanently modified.

Look for a source of water.  Broken or poorly sealed windows, air-conditioning, or water pipes should be repaired immediately.  Roof leaks and water fountains are also sources of high humidity.

Check for sources of fungus growth and spore production.  Heat exchange coils and water pans in air-conditioning systems are frequent sources of mold.  If mold is found in the air-conditioning system, turn it off to stop spore distribution.  Building Facilities Services must kill the mold and clean the system before it can be turned back on.

Detection

Often the first indication that a microorganism problem exists is a characteristic musty odor. A careful visual examination will generally locate stains that are clearly visible as pigmentations on a surface.

Another means of detection is by the use of ultraviolet (UV) light. Under UV light, a microorganism growth will appear luminescent. Ibid.

Recovery Procedures

Determine the cause and modify the environment.  Check the temperature and relative humidity.  If the temperature is above 75 degrees Fahrenheit, lower it to 65 – 70 degrees, if possible.  If the relative humidity is above 60%, bring it down to 50% or lower.  If the air-conditioning system merely lowers the temperature of the outside air prior to moving it through the building, turn it off – cooling the air without removing the moisture will increase the humidity.

Increase air circulation.  Dehumidifiers and fans can be used during a severe outbreak, but they are only temporary measures.  If such outbreaks are a recurring problem, then the environment must be permanently modified.

Examine sources of water.  Broken or poorly sealed windows, air-conditioning, or water pipes should be repaired immediately.  Roof leaks and water fountains are also sources of high humidity.

Check for sources of fungus growth and spore production.  Heat exchange coils and water panes in air-conditioning systems are frequent sources of mold.  If mold is found in the air-conditioning system, turn it off to stop spore distribution.  Maintenance must kill the mold and clean the system before it can be turned back on.

People have been known to have severe reactions to mold spores.  Since most people do not know if they are sensitive until they have had a reaction, it is best not to find out.  Everyone in a contaminated area and who is cleaning contaminated material must wear filter mask and gloves.  Everything that is affected or comes into contact with affected materials should be cleaned or thrown out.

Affected materials should be removed from the area so that other items are not contaminated.  The tables or anywhere else that moldy materials are to be placed should be covered with plastic sheeting.

The area must be cleaned before cleaned materials can be replaced in it.  If there is carpet, it should be dried and cleaned professionally.  Shelves, floors, walls, ceilings, and windows should be cleaned with a mold and mildew killing solution.

Mold can be removed from the cover of a dry book by taking the book outside, holding tightly away from you and vacuuming it with a small hand-held or canister-type, low-power (less that 1 - 1.5 horsepower) vacuum cleaner with a flexible hose.  Use the long, slender crevice tool and not the brush attachment.  Never attempt to vacuum mold inside, this will spread the spores.  Do not vacuum the surface of the pages.  When the vacuum bag is full, seal it and dispose of it in a safe container.  Do not use bleach solutions on books – it will bleach their covers and make matters worse by adding moisture.

A soft brush or rag may be used to gently brush or wipe the binding and text block.  Be careful not to brush the mold into air indoors or onto other objects.  Used rags should be sealed in safe containers and disposed of.  Used brushes should be sealed up until they can be disinfected.

Rags moistened with isopropanol alcohol can be used to wipe mold from the binding.  It should not be used on the text block.  A cotton swab moistened with isopropanol can be used to remove mold from the spine of a book with a hollow spine.  The book should then be placed upright in an open position and allowed to dry thoroughly.

Alcohol can be absorbed through the skin and nasal passages.  When using it, air circulation must be good and the windows should be open.

Alcohol can dissolve some finishes on furniture and dyes on materials.

If more than 100 items are affected or if more than 50 items are severely affected, they may need to be replaced. If they are to be retained, they should be sent to a commercial service for blast freezing.  Contact the service for information on the best way to pack and ship the items.

More on Mold

Many people are sensitive to mold. Also, some mold species are toxic. If any health effects are observed when treating mold consult a doctor or mycologist (the local extension service may be able to help) before proceeding.

The best way to prevent or stop an outbreak of mold is to remove items from environmental conditions that encourage mold growth: high temperature, high relative humidity, stagnant air, and darkness. The first priority is to dry moldy items (see instructions for drying below). If wet and moldy materials cannot be dried immediately freezing may stabilize them. Placing damaged items in a personal or commercial freezer will not kill mold. It will, however, put the mold in a dormant state until time and an appropriate treatment environment are available. Manageable quantities of frozen items may then be defrosted and treated at leisure.

Active mold looks fuzzy or slimy. Dormant mold is dry and powdery. Do not attempt to remove active mold; it may only spread or smear. Mold which remains active after freezing or after the host material appears dry may be treated with brief (1- 2 hours) exposure to ultraviolet radiation from the sun. Extreme caution must be exercised when treating materials outdoors: too much radiation will accelerate deterioration and may cause fading; wind may cause physical damage if items are blown about; and high relative humidity or condensation caused by quick temperature changes may actually exacerbate mold growth.

Dormant mold spores will reactivate as soon as conditions are favorable. They should, therefore, be removed from items and may be brushed or vacuumed away. This treatment should be performed outdoors where other materials and spaces will not be "infected." When brushing mold use a soft, clean, light-colored brush and a gentle pushing motion. Change soiled brushes often to prevent spreading mold from one object to another. When vacuuming, screening material placed over the nozzle of a low suction vacuum will capture loose bits of the item that may inadvertently dislodge. Ibid.

Treatment

Collections should be inspected regularly for signs of microorganism growth. If an object shows signs of infestation, the piece should be sealed in a polyethylene bag or enclosed in polyethylene sheeting to prevent the spread of spores to other objects. Remove the object to an isolated space where the RH can be lowered by running a dehumidifier.

A conservator should be contacted for assistance in dealing with the infested material. However, as a general procedure, vacuuming is appropriate in most situations. The object should be removed from the polyethylene and the bag or sheeting discarded. The object should then be vacuumed using a vacuum cleaner which will not exhaust the spores back out into the room. A vacuum fitted with a HEPA filter is recommended; however, the water bath filter vacuum cleaner, such as the Rainbow brand vacuum, that many parks have been using, is acceptable for this purpose. Follow all precautions when vacuuming an object: use the lowest effective suction and protective screening. Wear disposable gloves when handling a contaminated object. Seal the vacuum cleaner bag, gloves and other contaminated materials in a plastic bag and dispose of them in the trash outside the building. Also dispose of storage materials, i.e., acid free box or tissue, that were used to store the object.

For Further Reading

EPA Mold Remediation in Schools and Commercial Buildings Manual. Available online: http://www.epa.gov/iaq/molds/mold_remediation.html and http://www.epa.gov/iaq/molds  [Accessed February 24, 2004]

Hillery, Nancy.  1980.  “How to Prevent Mildew.”  In History News.  June:  58.

Nyberg, Sandra.  1987.  “The Invasion of the Giant Spore.”  SOLINET Preservation Program Leaflet No. 5.  Atlanta, GA:  SOLINET.

Pavon Flores, Sara C.  1975-76.  “Gamma Radiation as Fungicide and Its Effects on Paper.”  In Bulletin of the American Institute for Conservation of Historic and Artistic Works.  Winter:  15-44.

Wellheiser, Joanna G.  1992.  Nonchemical Treatment Processes for Disinfestation of Insects and Fungi in Library Collections.  Munich:  K. G. Saur.

Collapse of Shelving and Other Indoor Structural Accidents

Accidents involving the indoor structures of the Library, including the shelving units or walls, may occur due to several factors including tornadoes, fire, explosions, earthquakes, flood, and age.

Immediate Action

1.	Check for injuries first; take appropriate action.

2.	If a person is trapped, page Security (802-7022) and have them call 911.

3.	If there are minor injuries, page Security (802-7022).

4.	Clear other patrons from the area.

5.	Notify the Department Head and Library Director of the problem.

After

1.	Call Building Facilities Services (ext. 47494).

2.	Enter area when safe to do so as instructed by Building Facilities Services.

3.	Check for damaged material and begin recovery process by contacting the Disaster Recovery Team.

4.	Document all damage and recovery efforts with photographs.

5.	Contact Building Facilities Services (ext. 47494) to clean up debris.

6.	Evaluate shelving and area for structural damage and weakness. Replace any unsafe structures. Disaster Preparedness and Training Plan for Volpe Library Tennessee Technological University [Web page]

Theft and Vandalism

Prevention Activities

All vandalism of Library materials, facilities, or equipment is prohibited.  The best theft and vandalism prevention procedures begin with excellent security.  In order to ensure this security some simple precautions should be made.

APL, including AHC, provides a variety of materials to be used for educational and recreational purposes by any Library customer.  Vandalism of Library and Archive materials denies customers access to all the materials provided by the Library system.  Examples of vandalism include: Marking on or damaging Library materials in any way, and removing articles, pictures, pages or sections from Library materials.  The cost of replacing vandalized items prevents the Library from acquiring much-needed new material.  Most of the material in AHC is irreplaceable.

Theft

1.	The Austin History Center's intruder alarm system should be regularly tested, preferably by opening a window or door, instead of using a system self test.

2.	The security radio in the staff office area should be checked to be certain that messages can be sent as well as received.  Everyone on staff should know how to use the radio to call security.

3.	All researchers should follow the registration procedures as laid out by the Austin History Center.  When requesting research materials not kept in the Reading Room, researchers should fill out a call slip.  Staff should bring no more than four items or one box of photographs or manuscripts to the researcher at a time.

4.	Adequate procedures should be in effect to ensure that Reading Room staff do not have to leave researchers alone with materials.  No bags, briefcases or personal books should be allowed at tables and only pencils should be allowed in the room.

5.	Keys to buildings and special areas should be kept in a central location and their use monitored.  Administrators should keep an updated list of all employees holding keys and any key holders leaving the employment of the institution must return any keys they possess.

6.	Make sure to fill out an Incident Report form on Libro: http://libro/divisions/acao/security/incident/.

Vandalism

1.	The Library staff member who discovers a person suspected of vandalizing Library materials will alert the person in charge.

2.	Give the vandal a copy of the Library’s Statement of Policies, which prohibits “Abuse/vandalism of Library materials, facilities, or equipment.”

3.	Explain to the vandal that he/she is liable for a repair /replacement fee of $10.25 plus the cost of the item(s).

4.	Complete an Incident Report, including the vandal’s name and address, and the items damaged.  If the vandal refuses to provide a photo ID with name and address, ask him to leave the Library until he is willing to identify himself and pay the charges.

5.	Collect all damaged books, magazines, etc., including loose pages and articles and give them to the person in charge.

6.	Fax the Incident Report to Library Security (974-7469) and Library Administration (974-7403) within eight hours of the incident. Fill out and submit the Incident Report form on Libro: http://libro/divisions/acao/security/incident/.

Reading Room Security

Security procedures protect the collection by preventing theft or loss of materials.  Security is a constant negotiation of our requirements to maintain a safe collection while meeting the information needs of our patrons.  While we do not want to risk the safety of our collections, we do want to accommodate the information needs of our patrons.  We also want each of our patrons to leave with a favorable impression of our services.

Consistently following the procedures in the Policy and Procedures Manual along with the items in this list will help deter loss and theft of materials:

·	Allow loose paper only. Notebooks, clipboards, and pads of paper are not allowed.  Examine all of patrons' materials upon leaving.

·	Very few exceptions should be made.  When an exception is made, explain that it is being made.  For example, coin purses and billfolds of checkbook size may be kept by patrons in Reading Room, but items kept when larger than checkbook size would be an exception.

·	Pull no more than four folders, books, or items or one box of photographs or manuscripts per request at any one time.  When the patron has returned the four items, retrieve up to four more items for them. Routinely clear tables of materials when customers have completed their work with them.

·	At all times, one staff member should remain in the Reading Room.

·	Usually the biggest security problem patrons are not the ones who call attention to themselves by arguing or creating a scene.  Many times people have never visited archives and are merely surprised by our procedures.

·	Learning to "read" people and respond accordingly is essential for any public service job.  The technique you use might vary from patron to patron depending on their personality and yours.  For some people you may need to be forthright while with others a polite reminder or explanation will work.  The goal is to have every patron adhere to our policies.

·	An uncomfortable situation may be referred to a supervisor, but service cannot be denied unless a patron "uses violence or threatens to use violence or uses obscenities..." (A to Z, p. D1).  In this case, your supervisor and Security should be notified.  Notify Security to check the badges for those claiming to need exceptions to our procedures because they are police officers.

·	It is essential to watch patron activity and to be attentive to your surroundings.  It is useful to walk around or routinely scan the Reading Room while at the desk.

·	Remember, simply telling the patron "It is our policy" is not enough.  We need to explain the purpose of our policies ("We lock up belongings because we have one of a kind or fragile documents which are irreplaceable."

·	Be consistent!  This will help to establish our reputation as a public archives with equal access and service.

·	As part of the new security system AHC has "panic buttons" which can be used to summon help in the case of an emergency such as someone robbing the cash register or being engaged in some other form of dangerous lawbreaking in the Reading Room.  Press the button after the perpetrator has left -- no point in adding to the perpetrator’s anxiety level and endangering yourself.  One of these panic button devices is to be kept at all times on the top of RRI.  They immediately contact the police department in case of an emergency.  As soon as you push the button, it relays to the security panel of the Ground Floor that relays directly to APD that there is an emergency at the AHC.  That will send police officers here and will set off the silent security alarm throughout the whole building.

Emergency Procedures

If you suspect that a customer is vandalizing or stealing AHC materials, remember that we must prove that he has AHC property and that he intended to steal it.  Proving possession is easy, but proving intent is more difficult.  The most common way to demonstrate intent is to show that the thief concealed the item.  However, just because you cannot see it does not legally mean it is concealed.  To prove intent by concealment, the item has to be hidden in a place where it would not normally be carried.  AHC materials in a briefcase or backpack do not prove intent because the person could claim that he/she inadvertently scooped them up with personal papers.  AHC materials carried under clothing, or wrapped in something (like a jacket) can be used as a demonstration of intent:  Why would a person carry books under his shirt if he did not intend to conceal and steal them?

If you suspect that someone is trying to steal AHC materials or property, follow these guidelines:

·	Never assume that a person leaving AHC with materials intends to steal item.  Absent-mindedness or misunderstanding of AHC procedures are both reasonable explanations.

·	Approach people with courtesy, using non-accusatory words which objectify the situation:  “Excuse me, sir/madam.  Did you forget to return some materials?  Here, let me have them and I will return them.”

·	If the customer refuses to surrender the material, call Security.

·	If the customer tries to leave, do not risk injury to yourself by attempting to detain him/her.  Immediately write down a physical description of the person and give this to Security/police when they arrive.  If you know the person’s name and address, give this to security.

Recovery Procedures

As it is often said, the best recovery procedure is a good theft prevention plan, however sometimes even the best of these fail.  When theft or vandalism is discovered the following procedures should be followed:

Theft -call Security.  A police report should be filed.  Look through registration records to obtain the name and other information on the last person to use the material in question.

Vandalism of the building -call Security to make them aware of the problem.  Call Building Facilities Services to implement a clean-up procedure.  Take pictures of the damage in cases where insurance claims may be involved.

Vandalism of materials - Look through registration records to obtain the name and other information on the last person to use the material in question.  Make notes somewhere in the item record of the damage before it goes out to another patron.  Take pictures and contact a conservator to determine the most appropriate conservation procedures.  Complete an incident report and submit to the Library Services Manager.

For Further Reading

Austin Public Library A to Z.

Jenkins, John J.  1982.  Rare Books and Manuscript Thefts. Antiquarian Booksellers Association of America, New York.

Security from Loss: Water and Fire Damage, Biological Agents, Theft, and Vandalism. NDCC.

William Moffett.  March 1988.  “Guidelines Regarding Thefts in Libraries.” College and Research Libraries News, pp. 159-162.

Data Loss

Because the presence of digital information in libraries is a relatively new concept, not much procedural information is available on data loss and recovery.  The following are basic steps to take when digital information loss is discovered.

Prevention Activities

Only computer programs should be stored on individual computer hard drives.  All data essential to the operations of AHC, regardless of format, should be stored on the networked drives on the Austin Public Library’s server. The Library Server’s Libnwfs01 (File/Print Server) and Libnt01 (Primary Domain Controller) are both on a 3 week rotation, doing a full backup each day.  One set of Disaster Recovery tapes is kept at AHC, and the most recent week’s set kept in a safe.

Recovery Procedures

In the event of data loss, contact Jim Greco (974-7454 phone, 802-7038 pager or 974-7578 fax) to request the most recent back-up copy from the off-site storage facility.  Follow appropriate restoration procedures.

For Further Reading

ARMA.1987. International Guideline for Records and Information Management:  Magnetic Diskettes – Recovery Procedures.  Prairie Village, KS:  Association of Records Managers and Administrators, Inc.

Blackmon—Mooring—Steamatic Catastrophe, Inc., Special Technologies Division.  N.D.  Electronic and Magnetic Media Recovery.  Fort Worth, TX:  BMS—Cat, Inc.

Olson, Nancy B.  1986.  “Hanging Your Software Up to Dry”.  In College and Research Library News.  November:  634-636.

Hazardous Materials and Fumes

Immediate Action:  If you receive a warning signal, turn on a battery-operated radio or television for further emergency information.

If you suspect toxic fumes have been released in the History Center:

1.	Page Security (802-7022).

2.	DO NOT USE any electric equipment, including the public address system or elevators, if you smell natural gas.

3.	Clear the area or evacuate the building, if necessary. Try not to inhale gases, fumes, or smoke. If gas or vapors have entered the building, take shallow breaths through a cloth or towel.

4.	If appropriate, make public address announcement.  Repeat 2 times: "Attention! There are potentially toxic fumes in the building. Exit the building immediately! DO NOT USE THE ELEVATOR! If you need special assistance go to the 9th Street Exit and assistance will be given." (If known, substitute actual location of the fumes, and have users avoid that area during evacuation.)

5.	Follow the evacuation plan.

Precautions:

·	Try to stay upstream, uphill, and upwind of the accident.

·	Do not touch any spilled substances.

·	Stay away from accident victims until the hazardous material has been identified.

·	Help keep others away.

If Asked To Stay Indoors ("In-place Sheltering"):

1.	Make a public address announcement. Repeat 2 times:  "Attention! We have been informed that there are potentially toxic fumes (or hazardous materials)outside this building. For your safety, please remain in the building until further notice. Do not open any windows or doors."

2.	Close and lock windows and doors.

3.	Seal gaps under doorways and windows with wet towels and duct tape.

4.	Turn off ventilation system. Call Security (ext. 47401)

5.	Close off nonessential rooms such as storage areas.

6.	Fill large containers with water, then turn off intake valve to building, if possible.

Precautions:

·	If gas or vapors have entered the building, take shallow breaths through a cloth or towel.

·	Avoid eating or drinking any food or water that may be contaminated.

·	Monitor the local Emergency Broadcast System station for further updates, and remain in building until authorities indicate it is safe to exit.

Assisting Accident Victims

Precaution: Don't try to care for victims of a hazardous materials accident until the substance has been identified and authorities indicate it is safe to go near victims.

1.	Call for emergency medical care (9-911).

2.	Move victims to fresh air.

3.	Have victim lie down. Keep the victim warm. If breathing is difficult, a sitting position may be more comfortable. If unconscious, turn victim on his or her back and tilt head back. Turn head downward if victim is vomiting.

4.	If breathing has stopped, shout for help and begin CPR if you are qualified.

Evacuation:

Authorities will decide if evacuation is necessary based on the type and amount of chemical released and how long it is expected to affect the area. Other considerations are the length of time it should take to evacuate the area, weather conditions, and the time of day. Follow the Evacuation Plan for Exiting the Building as outlined.

If Asked To Evacuate:

1.	Stay tuned to local radio or television for information on evacuation routes, temporary shelters, and procedures.

2.	If you smell natural gas fumes, do not use the public address system or elevator.

3.	If appropriate, make a public address announcement. Repeat 2 times: "Attention! There are potentially toxic fumes in the building. Exit the building immediately! Go out the side emergency doors or the main entrance. If you need special assistance go to 9th Street Exit and assistance will be given." (If known, substitute actual location of the fumes, and have users avoid that area during evacuation.)

4.	Assist users out of the building, especially those requiring special assistance.

5.	Follow the routes recommended by the authorities. Leave at once.

6.	If time allows, minimize contamination in the building by closing all windows, shutting all vents, and turning off ventilation system.

7.	Take disaster supplies with you such as a flashlight with batteries, first aid kit and manual, essential medicines, emergency food, and water.

After

1.	Return to the building when authorities say it is safe.

2.	Follow local instructions concerning the safety of food and water.

3.	Clean up and dispose of residue carefully.

4.	Follow instructions from emergency officials concerning cleanup methods.  Disaster Preparedness and Training Plan for Volpe Library Tennessee Technological University [Web page]

Chemical Spills

As the AHC has a black-and-white photography laboratory in its basement, there are chemicals in the building. The photo lab contains the following chemicals:

Kodak Decktol developer

Kodak lens cleaner

Kodak sodium sulfite (anhydrous)

Sepia toner part A

Sepia toner part B

Kodak photo-flo 200

Kodak rapid fixer solution A

Kodak rapid fixer solution B

Kodak indicator stop bath

Kodak rapid selenium toner

Duro Navel jelly

Ilford 2000 RT developer

Ilford 2000 RT fixer

Formula 409 cleaner

Perma Wash solution

Ilford systems cleaner parts AB&C

Kodak developer D-76

Ivory dishwashing liquid

Prevention Activities

AHC materials that are not being copied photographically should not be stored in the photography laboratory. In general, it is usually more cost effective to replace library materials that have come in contact with spilled chemicals.  However, as most of AHC’s collection is irreplaceable, emphasis must be placed on prevention, rather than recovery.

Emergency Procedures

1.	Evacuate the room/area and ensure that people who are not involved in the response/recovery effort do not enter.

2.	Notify Facility Services.

3.	Complete an Incident Report Form.

4.	Take photographs to document damage.

5.	Prepare for recovery.

6.	Call Eastman Kodak for more information at 1-800-242-2424.

Recovery Procedures

Disperse fumes after a chemical spill.  Usually, the rate of air circulation should be increased.  The HVAC system should be turned off or the vents to the affected areas shut so that chemical fumes are not spread throughout the building.  Portable fans and open windows will help.

Terrorism

Emergency Procedures

Terrorism in General National Park Service. Disaster Plan. [Web page].

Terrorism can take a number of forms. Here are some general guidelines to follow when threatened. Recovery procedures will depend upon the nature of the terrorist act.

1.	Should an act of terrorism occur within the surrounding area:

2.	Follow the instruction of the Security and emergency preparedness personnel.

3.	If an explosion occurs, take cover immediately and anticipate there may be other explosions.

4.	Notify Authorities of any known hazards (e.g., fire, bomb threat).

5.	Stay indoors and away from windows unless directed to evacuate.

6.	Evacuate when directed and follow procedures included at the beginning of this booklet and any instructions of the Evacuation Coordinators.

7.	If released from work early, follow the instructions of the emergency preparedness personnel.  Do not remain in the vicinity to sightsee.

8.	Do not spread rumors.

Bomb Threat

The Austin Public Library’s Organizational Development section wrote a handout titled “Bombs as Terrorist Weapons-Employee Awareness” that is reprinted here in its entirety:

Bombs as Terrorist Weapons

Employee Awareness

This handout is based partially on information available from the Austin Police Department’s Bomb Squad and was prepared by the Austin Public Library’s Organizational Development section.  The APD Bomb Squad emphasizes the importance of “pre-planning” so that staff members know what actions to take in the event of a bomb threat or if they notice suspicious packages or materials in their worksites.  Supervisors and site managers should ensure that staff are familiar with procedures outlined in the APL Security Manual and should discuss emergency action plans with their respective staffs.  Contact APL Security with any questions about emergency procedures.  Note that in each situation, general instructions are given to contact APL Security and 911.  If APL Security is immediately available, they will instruct you as to how to proceed.  If they cannot be contacted immediately, call 911.  Also, always alert the supervisor in charge of the building site as soon as possible and notify the APL Director after emergency contacts have been made.

Introduction

Bombs were the weapons chosen for the attacks on the World Trade Center in New York City, the Federal Office Building in Oklahoma City, and the Centennial Olympic Park in Atlanta.  In late December 1999, President Clinton warned Americans to be vigilant against possible terrorist attacks over the holidays.  During that same time, 13 suspected terrorists were arrested in Jordan, and Algerian Ahmed Ressam was arrested at a U.S. border post with bomb-making equipment in his car trunk.  Nationwide, law enforcement officials have been alerted to the possibility of terrorist attacks.  While law enforcement agencies are tasked with protecting life and property, they need the assistance of citizens and employees within organizations.  Most bombs are homemade of readily-available materials (e.g., aluminum foil, ammonia, baking soda, cane sugar, cleaning fluid, Epsom salts, and vinegar) and are limited in their design only by the imagination and resources available to the bomber.  Therefore, employees who are familiar with their respective worksites are often the ones who may spot something unusual and suspicious.  Employees may also be the ones to notice people who are acting in a suspicious manner or may be the initial contact when a bomb is reported.

This handout will provide information to assist employees in detecting behaviors or items that may be unusual.  The intent of the information in this handout is not to scare our employees, but to:

a)	raise the awareness that the use of bombs as terrorist weapons could happen in the United States, in Texas, and in Austin,

b)	provide information to help staff recognize suspicious packages or letters that may contain bombs and to recognize suspicious behavior,

c)	know what to do if a bomb threat is received,

d)	know what actions to take to reduce the risk of injury or death to themselves and others in the event that a bomb is suspected or reported.

Placement of Bombs

Placement of bombs in a public facility may be accomplished by various methods.  They include delivery by an employee, customer, vendor or maintenance worker or even via a commercial carrier, private delivery service, or the U.S. mail.  They may be small and light enough to be easily concealed and carried in a purse, box, backpack, briefcase, or other container.  Bombs could be left at the loading dock, storage room, restroom, parking lot, elevator, or in plain sight on a table, bookshelf, or at the reception area.  Watch for anything unusual.  Refer to the section below on “Letter or Package Bombs” for more information.

What Does a Bomb Look Like?

Remember that a bomb may not look like what is normally visualized as a “bomb.”  In the bomb disposal business, a homemade bomb is referred to as an Improvised Explosive Device (I.E.D.).  The key to this description is in the word “improvised,” which means that no two individuals, without collaboration, would design the same I.E.D.  Using household materials and a bottle, pipe, or other readily available items, individuals can easily construct a bomb.  One search of Internet sites recorded more than 180,000 sites on explosives.  These ranged from pipe bombs to nuclear devices and one site alone contained more than 130 links to explosive formulas.  While it may be difficult to spot an item that looks like a “bomb,” staff should be alert for anything that looks unusual or out of place.  If an unusual or foreign object is encountered, under no circumstances should it be touched, tampered with, or moved.  Evacuate the area and call APL Security and 911, if appropriate.  Advice from APD’s Bomb Squad is that you should never move a suspicious package; rather, you should move the people away from the package.

Letter or Package Bombs

Letter or package bombs may be used in cases in which the goal of the bomber is to inflict injury upon a specific individual.  If any of the following is observed, do not open the package.  If a bomb is suspected, evacuate the area and call Library Security and 911, if appropriate.

Watch for the following:

1.	Balance.  In letter bombs, device components may shift and tend to unbalance an item of mail.  It may feel unusual as compared to other similar items of mail.

2.	Sweating.  Some chemicals used in explosives may “sweat” and result in “greasy” marks on wrappings.

3.	Odors.  Some of these chemicals also give off unusual odors, which the human nose will quickly sense.  For example, the Oklahoma bomb was constructed of nitrogen-based commercial fertilizer.  Nitrogen explosive devices may emit the same odor.

4.	Feel.  Letters have a normal “feel,” whereas those that contain devices may not “feel right.”  They may feel “stiff,” which could indicate the presence of plastic or metallic components as opposed to the normal paper stuffing.

5.	Packaging.  Be very cautious of envelopes or packages that are found within other packages.  This may be an attempt to mask or hide the actual explosive device.

6.	Lopsided packages.

7.	Wires protruding from a package.

8.	Addressing.  Be cautious of any of the following:

·	One which carries a strange place of origin, script, disguised or unusual writing or type, obvious misspelling or altering of words in the address field, or the lack of a return address.

·	Items marked “To Be Opened Only By,” or “Personal” or any other restrictive markings.

The Bomb Threat

Since the objective of terrorists is often to gain attention, it is likely that the first knowledge that a bomb has been planted may come from a phone call, recording, or written communication.  The majority of threats are called in to the target.  The caller may have definite knowledge that a bomb has been placed and wants to minimize personal injury or property damage.  Or, there may be no bomb and the caller wants to create an atmosphere of anxiety and panic.  Even if you think that the threat may be a hoax, never ignore a bomb threat.  Take every threat seriously and obtain as much information as possible.  Immediately report the threat and proceed with an evacuation of the building if appropriate.

Dealing with the Telephone Bomb Threat

A bomb threat may be made for two reasons.  Either the caller actually has knowledge of an explosive device or the caller wants to cause general alarm and panic.  Follow these steps for a bomb threat received by telephone:

1.	Remain calm, courteous, and listen.  Do not interrupt the caller.

2.	Use the form provided in the APL Security Manual to record as much information as you can.  Keep the caller on the line as long as possible to obtain details about the bomb.  Pay particular attention to background noises such as motors running, music playing, and any other noise which may give a clue as to the location of the caller.  Also note any distinguishing characteristics about the caller’s voice and mental state (calm, stressed, nasal, angry, deep, squeaky, any detectable accent, or the age and gender of the caller).

3.	If at all possible, gain the attention of other staff members so that they may begin contacting a) the manager in charge of the site, b) APL Security and c) 911 while you are still on the line with the caller.

4.	Immediately contact APL Security and 911 if another staff member was not already able to do so.  Remember to provide them with as many details as possible.  This is important, as often the more detailed the caller is with regard to the device and with information concerning the facility (e.g., accurately describes a room or exact location of furniture), the more likely that the threat may be real.

5.	Evacuate the building if instructed to do so by Security or the APD Bomb Squad.  If for any reason you are unable to reach them, report the situation to the person with the most seniority at the building site.  If the decision is left to you and you are not sure what to do, always proceed with the evacuation.

6.	Cooperate with emergency personnel by providing as much information as possible and in assisting in locating the reported bomb.

Receiving a Written Bomb Threat

1.	If a written threat is received, it should never be ignored.  Save all materials, including any envelopes or containers, and avoid further unnecessary handling.  Make every effort to retain evidence such as fingerprints, postal marks, and wrappings.

2.	Report the threat to APL Security and contact 911 if appropriate.

Suspicious Behavior

While knowledge that a bomb may have been planted may come from contact with the person who planted the bomb, also be aware of suspicious behavior that might indicate that a bomb or other type of weapon may have been planted.  Be especially aware of individuals who may have gained access to staff rooms, stairwells, hidden areas, or who may have purposely left packages or personal belongings (backpacks or bags) behind.

Evacuation

Never ignore a suspicious package, suspicious behavior, or an actual bomb threat.  Contact APL Security and 911 immediately once a bomb placement is suspected.  They will advise as to whether or not to evacuate the building.  However, if for any reason you are unable to contact them immediately or if it appears that immediate evacuation is needed, proceed accordingly.

1.	When announcing an evacuation, use “soft words.”  It is better to say, “We have a possible problem in the building and would like to ask you to leave for a few minutes while the situation is further evaluated” than to announce that, “There is a bomb in the building, so please evacuate.”  Notify employees and customers in a manner that will not incite panic, but assist them in moving quickly to the exits.

2.	Do not use the elevators.  Riders may be trapped in them or they may be needed for emergency workers to use.

3.	Move evacuated employees and customers as far away from the building as possible (a minimum of 300 feet).  Follow the “Fire Procedures” (as appropriate) outlined in the APL Security Manual for the evacuation.

4.	When leaving the building, employees should be alert for emergency equipment that may be arriving at the location.

5.	Leave the doors and windows open, if possible, to minimize primary damage from the blast and secondary damage from fragmentation.

6.	Leave the doors to the building unlocked, but assure that people do not approach nor try to enter the building until the situation has been resolved.

Searches

When it appears appropriate and if there is evidence that there is sufficient time, a search may be made.  Police officers may request the assistance of staff to help conduct the search.  Employees familiar with the area may be able to more quickly spot unusual or foreign objects.

Handling of the News Media

Refrain from discussing the situation with anyone, including the news media, until an investigation has been made.  If approached by members of the news media, refer them to one of the following individuals:

Brenda Branch, APL Director

Tom Moran, APL Associate Director

John Gillum, Facilities Services Manager

Sources Used to Develop This Handout:

Austin Public Library, Security Manual, Austin, Texas.

Kennish, John W., CPP – Security Consultant, 62 East Pond Meadow Road, Westbrook, Connecticut 06498, 1999.

Internet site:  http://kennish.com/bombthreat

National Security Institute’s Security Resource Net, 57 East Main Street, Suite 217, Westborough, Massachusetts 01581.

Internet site:  http://nsi.org/Library/Terrorism/bombthreat.html

Neilson, Jim.  Bomb Squad, Austin Police Department, Austin, Texas.

Trump, Kenneth S., Management Strategies, February 1999.  School Planning & Management Magazine, 330 Progress Road, Dayton, Ohio, February 1999.

Internet site:  http://www.spmmag.com/articles/Feb99/article0180.html

Nuclear, Biological and Chemical Weapons

The Austin Public Library’s Organizational Development section wrote a handout titled “NBC Domestic Preparedness Training Program -Employee Awareness” that is reprinted below in its entirety:

NBC Domestic Preparedness Training Program Employee Awareness

This handout is based on information available from the City of Austin’s Emergency Management Office and was prepared by the Austin Public Library’s Organizational Development unit to help APL staff increase awareness of the types of NBC weapons and to know what actions to take if use of these weapons is suspected.  Supervisors and site managers should discuss emergency action plans with their respective staffs.  Contact APL Security with any questions about emergency procedures.

Introduction

The threat of terrorism is alive and growing, and one group of weapons that may be used by terrorists is known as “NBC,” which stands for “nuclear, biological, and chemical.”    The Federal Bureau of Investigation (FBI) defines terrorism as “the unlawful use of force or violence against persons or property to intimidate or coerce a government or civilian population, in furtherance of political or social objectives.”  While bombs were the weapons chosen for the attacks on the World Trade Center in New York City, the Federal Office Building in Oklahoma City, and the Centennial Olympic Park in Atlanta, the 1995 terrorist attack in the Tokyo subway system involved the use of nerve agent sarin.  The cult responsible for the sarin attack was developing biological agents as well.

In 1996, Congress enacted a law establishing the Domestic Preparedness Program.  The goal of the program is to ensure that we are prepared to respond to terrorist attacks involving NBC weapons.   One way that an organization may prepare is by providing information to employees who may be the first to notice anything unusual in their worksites.  Because urgent medical treatment is needed immediately following an attack, lives may be saved by raising the awareness, helping employees to recognize signs, and providing procedures for employees to follow in the event of an attack.

The intent of the information in this handout is not to scare our employees, but to:

a)	raise the awareness that the use of NBC weapons could happen in the United States, in Texas, and in Austin,

b)	to provide information to help staff recognize signs of NBC weapons, and

c)	to know what actions to take-in the event of an attack-to reduce the risk of injury or death to themselves and others.

NCB Weapons

| Type of Weapon | What They Are | How They Enter the Body | Signs & Symptoms | Indicators of an Attack |
| --- | --- | --- | --- | --- |
| Nuclear Materials | Materials that produce radiation | Breathing in, swallowing contaminated food or water, absorbing through the skin | Generally none unless exposed to massive amounts. In that case, symptoms include burned and reddened skin, nausea, vomiting, diarrhea, hair loss, convulsions, unconsciousness (symptoms usually occur between 30 minutes and a few hours) | Radiation is invisible and odorless and requires special equipment to detect. There may not be obvious signs. |
| Biological Materials | Living organisms or products of living organisms that can be deadly if undetected. Three categories: Bacteria or Viruses that cause diseases such as Anthrax or Smallpox; and Toxins, which are poisonous products of living organisms such as snake venom or food poisoning | Breathing in, through breaks in the skin, eating or drinking contaminated food or water | Different for each agent, but some general symptoms: Coughing, flu-like symptoms, shortness of breath, weakness or fatigue, vomiting, diarrhea. Symptoms may take hours or days to show. If contagious, others could be infected. | Some indicators: Unusual amount of people with flu-like symptoms, especially in off-season; unusual or unscheduled insecticide-like spraying; abandoned spraying devices; several people suffering food poisoning-like symptoms such as vomiting and diarrhea; or a terrorist calls and reports an attack. |
| Chemical Materials | Materials designed to kill or severely injure; similar to household chemicals (chlorine and pepper spray are examples) but much more hazardous; they are easy to obtain and cheap. They attack the central nervous system, respiratory system, skin, eyes, and mucous membranes. | Breathing in, by direct contact with skin and eyes, eating or drinking contaminated food or water | Red, irritated eyes and skin; choking; coughing; shortness of breath; vomiting; nausea; runny nose; dizziness; loss of consciousness; seizures; pinpointed pupils; dimness of vision | Easiest of the three to recognize; immediately noticeable effect: Groups with unusual behavior or symptoms; abandoned spraying devices (fire extinguishers or aerosol cans) or packages; unusual fogs, clouds, or mist, especially indoors; pools of liquid with no known source oozing from bags or backpacks; strange smell; an explosion |

Take These Actions If You Suspect NBC Weapons Have Been Used

1.	Observe your surroundings:

Are there any unusual pools of liquid on the ground?

Has anyone reported an unusual smell?

Do you see any strange fogs or clouds indoors?

Do you see any unusual devices or things out of place lying around?

Do you observe any unusual behavior or signs of distress (medical symptoms)?

Do you notice a large number of dead animals or insects (environmental signs)?

2.	Follow your organization’s emergency plan:

At all Austin Public Library sites, refer to the procedures outlined in the APL Security Manual and in the Workplace Violence Prevention Information and Contacts sheet.  For most situations, the manual will instruct you to contact APL Security (if time permits) or to call 911.  Do not attempt to remove any suspicious-looking items, but do evacuate the building if any NBC materials are suspected.

3.	Protect yourself:

a)	Cover your nose and mouth with a cloth and take frequent, shallow breaths.  Do not attempt to smell, eat, or touch any materials.

b)	Self-decontaminate by removing outer clothing and washing with cold water and soap if possible.

c)	Get yourself and others away to safety before contacting authorities.

4.	Notify authorities:

Provide the following information to authorities when you call 911.

*Location of incident

*Number of victims

*Symptoms

*Indicate if there was a fire or explosion

*Type of vehicle or containers

*Specify indicators (explain why you think this may be an NBC attack)

*Meeting place for emergency responders to locate you

Note:

This handout is based primarily on information contained in the NBC (nuclear, biological, and nuclear) Domestic Preparedness Training Program video available through the City of Austin’s Emergency Management Office.

Explosion

Emergency Procedure

In case of an explosion in your area:

1.	Remain calm.

2.	Take cover under a table or desk.

3.	Be prepared for possible further explosions.

4.	Stay away from windows, mirrors, overhead fixtures, filing cabinets, bookcases, etc.

5.	Follow the instructions of the security guards and emergency preparedness personnel.

6.	Evacuate calmly, when directed, to the Assembly Area.  Assist disabled persons.

7.	Do not move seriously injured persons, unless they are in immediate danger (fire, building collapse, etc.)

8.	Open doors carefully.  Watch for falling objects.

9.	Do not use elevators.

10.	Avoid using the telephone, except in a life threatening situation.

11.	Do not use matches or lighters.

12.	Do not re-enter the affected area until directed by emergency preparedness personnel.

13.	Do not spread rumors. National Park Service. Disaster Plan. [Web page].

Recovery Procedures

Recovery operations take place after the source of the emergency has been dealt with and the building is safe to enter.  Recovery is likely to be based on a mix of commercial services, University of Texas staff knowledge and assistance, and in-house capabilities.  The following steps are the general steps to be taken during recovery.  Specific instructions are given in each emergency section.

1.	Assess the damage.

2.	Remove materials after the insurance adjuster indicates that it is all right to do so.

3.	Stabilize the environment.

4.	Restore the area.

5.	Make decisions about collections:

a. withdraw

b. use as is

c. clean materials

d. repair it in house

e. send to conservators

f. send to commercial companies

6.	Salvage collections.

Explosion Damage

When the situation is safe, the building and services have been established and re-entry to the site is permitted, commence immediate disaster actions.

Immediate Actions

The Library Services Manager in consultation with Building Facilities Services assesses the situation to:

·	Establish if collection material has been affected and in what way

·	Check that shelving and fittings are structurally sound

·	Check the need for short term protection of the collections from water, theft, exposure to fluctuating outside

·	Environmental conditions

When the situation has been assessed, commence short and long term response actions.

Short Term Response and Long Term Recovery Actions

Where collection material has been water affected it will be treated as water affected.  Follow directions in the sections of this plan on water damaged materials.

Where material has not been water damaged but is blast damaged, the Library Services Manager assesses situation and, in consultation with Building Facilities Services and Collection Managers, will determine a strategy for salvage priority is given to items of particular local significance and unique material.

Where windows and / or external walls have been blown out:

·	The Library Services Manager and Building Facilities Services consult on the most appropriate means of protecting the collection against the elements and against unsuitable environmental conditions

·	Building Facilities Services arrange for stabilization of the building environment if practicable

·	otherwise, the Library Services Manger arranges for movement of particularly vulnerable material and covering of collections

When short and long term actions are completed:

The Library Services Manager and Building Facilities Services conduct a full post-disaster assessment to:

Analyze the successful and failing aspects of the immediate, short and long term actions taken

Prepare a written report on the incident including:

Cause of the disaster

Number of items damaged, replaced, discarded, and repaired

Ongoing treatment costs

Impact on service provision to clients

Staff time expended during the operation

Cost of restoring the affected area

Cost of equipment and supplies

Make changes to the disaster plan where necessary

Propose changes to security and building management procedures if necessary

Send letters of thanks to those who assisted  National Library of Australia NLA collection Disaster Plan [Web page].

Severe Storms

Prevention Activities

Weather Definitions From KVOO Classic Country AM - 1170 in Tulsa, Oklahoma. "Weather Definitions" [Web page] http://kvoo.com/defin.htm [No longer available - last accessed November 30, 2000]

Summer

Downburst: An exceptionally strong gusty wind from a thunderstorm that may cause property damage. Downburst winds can produce damage similar to a tornado. Also called a "microburst" or a "macroburst," depending on the amount of area affected.

Dry Line: A boundary that separates warm dry air from warm moist air. Often represents a zone of instability along which thunderstorms form.

Flash Floods: Flooding that results from very heavy rainfall in a short period of time.

Funnel Cloud: A rotating, cone like cloud that extends from the base of a thunderstorm (not touching the ground).

Gust Front: A moving boundary of cool air that flows out of the base of a thunderstorm, spreading out along the ground ahead of the actual storm. Often the passage will resemble that of a cold front.

Hailstones: Transparent or partially opaque particles of ice that range in size from that of a pea to softballs.

Lightning: A visible electrical discharge produced by thunderstorms. Lightning may take place within a cloud, cloud to cloud, cloud to the surrounding air or cloud to ground.

Roll Cloud: A low, horizontal tube shaped cloud associated with a thunderstorm gust front.

Severe Thunderstorm: Severe thunderstorms produce winds of 58 MPH or greater and/or hail 3/4 (about dime size) or larger.

Squall Line: A long narrow band of active thunderstorms.

Straight Line Winds: Non-rotating winds associated with thunderstorms, most frequently found in advance of the gust front at the leading edge of the thunderstorm. These winds rapidly spread out becoming strong horizontal winds. Often do as much damage as tornadoes.

Supercell: A thunderstorm with a rotating updraft, especially at middle levels. The rotation can often be seen by Doppler radar. Super cells produce most strong and violent tornadoes and also can produce damaging straight line winds, giant hail and flash flooding.

Tornado: A violent rotating column of air that extends from the base of a thunderstorm to the ground, in the shape of a funnel or rope. Winds can exceed 300 MPH in the most powerful tornadoes. Tornadoes vary in size from a few feet across to over a mile wide.

Thunderstorm: A local storm, accompanied by lightning and thunder, produced by a cumulonimbus cloud, usually with gusty winds, heavy rain and sometimes hail.

Wall Cloud: An area of rotating clouds that extends beneath a severe thunderstorm. Usually one to four miles in diameter. A wall cloud usually develops before a funnel cloud or tornado.

Watch: A statement issued by the National Weather Service for potential tornado, severe thunderstorm, or flash flood conditions. A watch identifies a relatively large area in which severe weather may develop.

Warning: A statement issued by the National Weather Service for tornado, severe thunderstorm, flash flooding or river flood conditions. A warning is issued when one of the weather types already exists and/or has been spotted or indicated by Doppler radar. Warnings are statements of imminent danger.

Winter

Advisory: Issued by the National Weather Service to indicate that winter weather is expected to cause significant inconveniences and could become hazardous. If precautions are taken, these situations should not become life threatening. The greatest hazard is often to motorists, so it normally is advisable to avoid unnecessary travel or at least use extra caution and allow extra travel time.

Black Ice: Patches of solid clear ice that form on road surfaces and typically appear darker than nearby dry surfaces. Black ice often does not look like ice at all, especially at night, and therefore poses a significant hazard to motorists.

Blizzard: A combination of wind and snow resulting in extremely hazardous weather. Technically, a blizzard must have sustained winds or frequent gusts over 35 miles per hour and visibility frequently less than a quarter mile in falling and/or blowing snow, along with life-threatening wind chills. These conditions must prevail for three hours or more before a winter storm becomes a blizzard.

Blue Norther: A strong cold front accompanied by significantly colder air and strong northerly winds. The word "Blue" is believed to reflect the significant temperature drop, but may also refer to the deep blue skies that sometimes accompany the colder air.

Flurries: Light snow falling for short duration and resulting in little or no accumulation.

Freezing Rain: Liquid rain that falls into a layer of sub-freezing air near the ground, and therefore freezes on contact with objects that have cooled to below freezing. If the layer of cold air near the ground is deep enough or cold enough, the raindrops may freeze into ice pellets or sleet before reaching the ground.

Graupel: Same as Snow Pellets.

Snow (accumulation): Defined in Oklahoma and Texas as an accumulation of 4 inches or more in 12 hours, or 6 inches or more in 24 hours. Amounts that qualify for Heavy Snow generally are lower in the Southern U.S., where snow is less frequent, and greater in northern states where it is more common.

Heavy Snow (observations): Falling snow that reduces the visibility to a quarter mile or less.

Ice Pellets: Same as Sleet.

Ice Storm: Heavy accumulations of ice resulting in significant structural damage, including downed tree limbs and/or utility lines. Significant disruption of travel can be expected.

Light Snow: In weather observations, this refers to falling snow in which visibility is 5/8 of a mile or more. In forecasts, it refers to a relatively steady fall of snow that generally results in light accumulations or none at all.

Moderate Snow: In weather observations this refers to falling snow that reduces the visibility to less than 5/8 of a mile but more than 1/4 mile.

Norther: In general a cold wind from the north. In the Southern Plains, it normally refers to either a strong cold front during the winter months or the colder air and northerly winds behind it. A strong norther can drop the temperature 25 degrees or more in an hour or 50 degrees or more in less than a day. Wind chill temperatures may fall even more.

Sleet: Pellets of ice resulting from raindrops falling into a layer of subfreezing air, and therefore freezing before reaching the ground. If the raindrops do not freeze before reaching the ground, they may freeze upon contact with the ground resulting in freezing rain.

Snow Grains: Small white particles of ice. They are similar to snow pellets except they are smaller and do not shatter or bounce when they hit a hard surface.

Snow Pellets: Precipitation consisting of white, opaque particles (unlike ice pellets or sleet, which normally are clear) that are typically round or conical in shape. They often resemble miniature snowballs, and unlike snow grains will normally bounce or break up when they fall on a hard surface. Also sometimes called Graupel or Tapioca Snow.

Wind Chill: A measure of the combined effects of cold air and wind on exposed skin. As wind increases, heat is carried away from the body at a faster rate making it feel even colder. The wind chill temperature is the same as the air temperature as long as the wind speed is 4 miles per hour or less. Otherwise, it is less than the air temperature.

Winter Storm Warning: Issued by the National Weather Service to indicate that hazardous and life-threatening winter weather, such as heavy snow or an ice storm, either is occurring, will soon begin, or has a very high probability of occurrence. Stay indoors unless absolutely necessary.

Winter Storm Watch: Issued by the National Weather Service to indicate that the risk of hazardous and life-threatening winter weather has increased significantly, but it's occurrence, location, or timing are still uncertain. Begin preparations and listen for further information.

Emergency Procedures

These first procedures apply to thunderstorms, tornadoes, hurricanes, etc.

Storm Watch

1.	In the event of a severe storm watch within the surrounding area:

2.	Listen to the local radio/TV or NOAA Weather Radio for instructions.

3.	Plan ahead before the storm arrives.

4.	Tie down loose items located outside or move them indoors.

5.	Open windows slightly, time permitting, on the side away from the direction of the storm's approach.

6.	Check battery-powered equipment and back up power sources.

Storm Warning

1.	Disconnect electrical equipment and appliances not required for emergency use.

2.	Do not use telephone except for an emergency or absolutely essential business.

3.	Store drinking water in clean containers (e.g., jugs, bottles, sinks).

4.	Avoid structures with wide span roofs (e.g., gymnasium).

5.	Otherwise, take cover.

Tornado

Tornadoes are common events in Central Texas. If staff is notified or observes a tornado approaching, follow these guidelines:

1. Stay away from windows and doors.

2. Take refuge in a small room with strong walls, such as bathroom, interior closet, hallway, or stairwell, or in a basement. Upper floors are not safe.

3. If possible, wrap yourself in a blanket to protect your eyes and face.

4. If additional protection space is needed, advise customers to take refuge in doorways or near mechanical rooms with steel structures, and to cover their faces and eyes.

Tornado Watch:

A tornado watch means there is a good possibility of severe thunderstorms developing tornadoes.  A watch is usually in effect for a period of several hours and covers a large area.  Although a tornado watch can be issued and tornadoes not occur, you need to be aware of quickly changing conditions during stormy weather because tornadoes can, and do, occur abruptly.

Tornado Warning:

A tornado warning means that a tornado is on the ground, has been sighted, or has been indicated on radar.  A tornado warning is usually in effect for a very short time and typically covers only a small area.  You should consider a tornado warning as an emergency situation.  Seek inside shelter immediately.

Winter Storm

If a winter storm warning is issued for the area:

If at work --

·	Listen to the local radio/TV for weather advisories and official permission to go home early.

·	Plan ahead before the storm arrives.

·	Move indoors any items located outside which might be damaged by the storm or become hazardous during high winds.

·	Check all battery-powered equipment and back up power sources.

·	If you must travel (business or going home), use public transportation if possible.  If not and you must drive:

·	Make sure the vehicle is in good condition, equipped with chains or snow tires, and has a full tank of gas.

·	Take another person with you, if possible.

·	Leave an estimated itinerary (destination and estimated time of arrival) with someone.

·	Have emergency "winter storm supplies" in the vehicle (e.g., sand, shovel, windshield scraper, tow chain or rope, flashlight, flares.  It's also good to have a blanket, heavy gloves, overshoes, extra woolen socks, and winter headgear).

·	Travel by daylight and use major highways, when possible.

·	Keep the radio on for weather information and advice.

·	Don't be daring or foolhardy.  Rather than risk stalling, lost, or isolated, stop, turn back or seek help if conditions threaten to test your ability or endurance.

·	If the vehicle breaks down, or you become lost, or stalled:

·	Don't panic!  Think the situation through, and decide the safest and best thing to do.  Then do it slowly and carefully.

·	If on a well traveled road, indicate you are in trouble (e.g., hazard flashers, raised hood, hanging cloth from radio aerial or window.  Then stay in the car and wait for help to arrive.  If you run the engine to keep warm, keep snow away from the exhaust pipe and keep a window open enough to provide sufficient ventilation.

·	Wherever you are, if there is no house or other source of help in sight, do not leave the car to search for assistance.  It is very easy to become disoriented and lost during a severe storm.

If at home

Listen to the local radio/TV for weather advisories. Plan ahead before the storm arrives; prepare for possible isolation for a couple of days.  Ensure you have on hand or the proper working condition of:

·	Blankets

·	Some kind of emergency heating equipment and adequate supply of fuel

·	Food and water, emergency cooking equipment. (It's better to have some foods that do not require cooking or other preparation)

·	Battery-powered radio and extra batteries, flashlights/lanterns and extra batteries/fuel; and

·	Simple tools for fire fighting.

·	Move indoors any items located outside which might be damaged by the storm.

·	Fill vehicle gas tanks.

·	Travel only if absolutely necessary and follow precautions shown above.

Recovery Procedures

Recovery operations take place after the source of the emergency has been dealt with and the building is safe to enter.  Recovery is likely to be based on a mix of commercial services, University of Texas staff knowledge and assistance, and in-house capabilities.  The following steps are the general steps to be taken during recovery.  Specific instructions are given in each emergency section.

1)	Assess the damage.

2)	Remove materials after the insurance adjuster indicates that it is all right to do so.

3)	Stabilize the environment.

4)	Restore the area.

5)	Make decisions about collections

a. 	withdraw

b. 	use as is

c. 	clean materials

d. 	repair it in house

e. 	send to conservators

f. 	send to commercial companies

6) Salvage collections.

For Further Reading

Hunter, John E.  1986.  “Museum Disaster Preparedness Planning.”  In Protecting Historic Architecture and Museum Collections from Natural Disasters.  Barclay Jones, ed.  Boston:  Butterworth: 211-230.

National Oceanic and Atmospheric Administration.  1992.  Tornadoes – Nature’s Violent Storms:  A Preparedness Guide.  NOAA/PA 92052, ARC 50002.  Baltimore, MD:  NOAA.

Ruffner, James A. and Frank E. Bair, eds.  1987.  The Weather Almanac.  Detroit:  Gale Research Company.

Major Traffic Accident

Major transportation accidents are those involving any of the various modes of transportation (e.g., highways, waterways, railways, and airways). Such accidents could occur at any time and any place, and often involve multiple injuries and/or deaths.

Many facilities are not prepared (and are not expected to be prepared) to cope with the type of problems created by a major transportation accident. Should such a disaster occur, initiate life-saving and property protection actions until assistance can be provided from the community. For example, security personnel are trained to extinguish small fires and to ensure the safe evacuation of the public. The medical staff and/or persons trained in first aid can attend injured persons. Also, during regular work hours, the staff can implement appropriate measures to protect the collections and other physical assets. National Park Service.

Disaster Planning Web site for Primer on Disaster Preparedness, Management, and Response: [http://www.cr.nps.gov/museum/publications/primer/primintro.html].

Technical Disasters: Transportation Accidents

A transportation accident may damage the Library building and a part of its contents, or release hazardous fumes in the area.

Immediate Action:

A. Evacuate the area of the building damaged.

B. Check for injuries.

C. Call Security at 802-7022 and APD at 911 to report damage. State your location (Austin History Center, 810 Guadalupe) and estimate extent of damages and report injuries.

D. If hazardous materials are detected, follow Disaster Preparedness and Training Plan for proper procedure.

After:

A. When safe to do so, assess damage to materials, equipment and building.

B. Document damage and recovery efforts with photographs.

C. Protect areas open to the weather with plastic sheeting, and remove materials from that area.

D. Contact Library Services Manager (974-7388). Disaster Preparedness and Training Plan for Volpe Library Tennessee Technological University [http://www2.tntech.edu/library/web_guides/displan.HTML].

Bibliography

Austin Community College.  1996.  Emergency Preparedness Plan.  Austin, Texas.

Austin History and Records Center.  1995.  The Austin History Center:  The Building that a Community Made Possible.  A public information flyer.

Austin Public Library.  A to Z.

Austin Public Library.  Security Manual

Brand, Marvine, editor.  1984.  Security for Libraries.  Chicago:  American Library Association.

Fortson, Judith.  1992.  Disaster Planning and Recovery:A How-To-Do-It Manual for Librarians and Archives.  New York:  Neal-Schuman Publishers, Inc.

Kahn, Miriam. 1995.  First Steps for Handling & Drying Water Damaged Materials. Columbus, Ohio: BMK Consulting.

Lincoln, Alan Jay.  1984.  Crime in the Library:  A Study of Patterns, Impact, and Security.  New York:  R. R. Bowker Company.

Morris, John.  1986.  The Library Disaster Preparedness Handbook.  Chicago:  American Library Association.

Olkowski, William, Sheila Daar, and Helga Olkowski.  1991.  Common Sense Pest Control.  Newton, CT:  The Taunton Press.

Steed, Kay.  Designing a Disaster Plan:  The Top Ten Elements of a Disaster Plan.

Walls, David.  1995.  A Disaster Prevention Risk Assessment Program for the Austin History Center.  A paper completed for LIS  388K.12, The University of Texas at Austin.

Walsh, Betty.  “Salvage Operations for Water Damaged Collections.”  Western  Association for Art Conservation Newsletter.  Vol. 10, No. 2.

Consult the Web for:

Library of Congress’ Web site: http://www.loc.gov/preserv/pubsemer.html.

Conservation OnLine http://palimpsest.stanford.edu has disaster plans from a number of library and archival institutions

Society of Rocky Mountain Archivists Web site http://www.srmarchivists.org/preservation/resources.htm for disaster recovery information in a database searchable by the type of disaster.

National Park Service Disaster Planning Web site for Primer on Disaster Preparedness, Management, and Response: http://www.cr.nps.gov/museum/publications/primer/primintro.html

Northeast Document Conservation Center:  http://www.nedcc.org

Vidipax Company web site: http://www.vidipax.com/.  Video- and audiotape restoration service.

Planning for Disaster

Last Updated: 11/2006

1. Do you have up-to-date floor plans for your building? Yes _X  No__

If yes, are they clearly marked with location of:

Fire extinguishers   Yes _X  No_

Fire alarms 	Yes_X__  No___

Emergency exits     Yes_X_   No__

Master switches for electricity 	Yes__   No X

Note: ACFS has asked that staff NOT touch the emergency cutoff for electricity. Many of our systems are inter-connected and will cause extra problems if not disconnected properly. The emergency cutoff  for electricity is outside the staff entrance (on the south side of our building.) Please contact Security and they will get ACFS to handle the emergency.

Water main shut-off   Yes__ No X_

Note: ACFS has again asked we NOT touch the emergency cutoff for the water. It is connected to other systems as well. The emergency cutoff can be located by exiting the 9th St. doors and looking immediately on the ground to the LEFT of the stairway. There are a couple of square shaped metal plates on the ground there and the emergency water cutoff is under one of those plates.

2.   Do you have a staff/patron evacuation plan? Yes_X_   No_____

Is it up-to-date? Yes__X__   No_______

Are staff members aware of their roles in the event of a fire, bomb threat or other emergency? Yes_______ No______   Check and update at meeting

Are floor plans with emergency exit routes posted in public areas of your library?

Yes__   No X__

We suggest that extra copies of the evacuation plans be made, in yellow cardstock type paper, and be placed prominently in every room of the history center.

3.    Do any of your stack ranges sit directly next to an interior wall? Yes_X___   No______

Do books or other materials rest within 2" of that wall? Yes__X___   No______

If yes, please identify the location and give an estimate of the numbers of volumes involved:

Several

4.      Do any of your stack ranges sit directly next to an exterior wall?  Yes__X_No______

Do books or other materials rest within 12" of that wall? Yes__X___  No_____

If yes, please identify location and give an estimate of the number of volumes involved:

Several

5.	Do you have any works of art or other materials hung on exterior walls?  Yes_X  No _

If yes, please identify location and give an estimate of the numbers and types of items involved.

* Another important practice is the scheduled review of emergency and disaster plans with each Department.  At least annually, two members of the Disaster Recovery Team will meet with each unit to review the Security Manual and the Disaster Plan to insure that the procedures are familiar to all.   University of California at Davis Disaster Prevention, Preparedness and Recovery Plan [Web page]

Building Survey

Last Updated:11/2006

ARCHITECTURE

1.   Type of primary building material (brick, concrete, etc.)

Foundation and walls: Limestone

2. Foundation: visible water stains? Yes_X__No___   If yes, describe location and extent of stains. Are there cracks? Yes_X__ No___   If yes, describe location and extent of cracks:

*	Are collections stored in basement areas? Yes_X_ No___ Is there seepage into basement areas?  Yes_X__ No__

If yes, describe location and extent:  Water team is addressing this issue.

The staff room did experience a flood of 1-2 inches of water in 2006 - I believe it was due to some backup in pipes to the kitchen sink.

3.    Roof: type of building material: Asphalt

Flat roof? Yes _X_   No___   Skylights? Yes___ No _X_Drains/Eaves? Yes_X_ No___

Condition?  Replaced in 2003

Evidence of leakage through ceilings? Yes_X__ No__   Where?

Most recent leak? Water team assessing this information.

Extent of damage to collections: None in 2006

5.   Do you experience ongoing problems related to the building structure not mentioned above? Yes___ No _X_

If yes, please describe:

Risk Assessment Form:  Fire

Evacuation Plan						 	Last Updated:11-2006

Comments:

The evacuation plan has been updated to show emergency exits and location of fire extinguishers.  At this writing, there are none posted in the rr area or general stacks location.  I would make a suggestion that one be posted in areas of the building to assist in the event of an evacuation.

Fire Inspection							LastUpdated:11-2006

Comments:

Lt. Panacci of the Austin Fire Department came to the Austin History Center on November 8, 2006 to conduct a routine inspection of our building.  Among the things noted in his report were the following:

HAZARD CODE 1-B – room g-22 (AMN video) boxes need to be lowered to 24” below ceiling.

HAZARD CODE 3-D- a/v room basement and east exit-remove thumb turn lock with panic bar hardware

HAZARD CODE 1E-basement-remove boxes in corridor  (boxes have been removed and placed in the basement of Faulk for storage  11-2006)

HAZARD CODE 2A-Mayor’s Room needs to have a fire extinguisher installed (fire extinguishers have been installed in the Mayor’s room 11-2006)(contact  - Lee Dawson in security to have them properly mounted)

HAZARD CODE 1B-stacks 108 lower storage to 24” below ceiling.

A time frame of 21 days from the date of inspection was given to have identified hazards corrected.

Fire extinguishers

Fire extinguishers are located throughout the building. See Evacuation Diagrams, pp. 32-34 for locations of fire extinguishers.

Ground Floor:  Art Rack Room, Exhibit Specialist’s Office (inside entrance from the kitchen), Hallway (next to water fountain near kitchen), Architecture Archives (on column in middle of room), Closet behind elevator (next to Ladies Restroom), Travis County Records, Hallway leading to parking lot (next to Photo Lab entrance), Photo Lab (inside entrance), Photo Lab (Printing Room), Photo Lab (Hallway near stairs), Video area (by steps leading to raised office area in northeast work room), Video area (inside entrance to the southeast work room.

First Floor:  Reading Room (next to swinging door), Staff Work Area (inside, by swinging door), Microfilm Room, Photo Room, Stacks (on north wall), Archivist Office (inside entrance), Kitchen, Reception Room (east side of fire place), Archives Room (inside entrance), Across from Elevator, Stairwell leading down to Architectural Archives.

Second Floor:  Archives Balcony (on left as you exit to stacks), Stacks (on north wall), Staff Office Area (to right of entrance to Public Service Librarian’s office).

Third Floor:  Inner Vault (on left as you enter), Outer Vault (by door leading to stairwell).

Watch for these fire hazards:

*	smoking in the building

*	combustible draperies and carpet

*	Christmas trees and other decorations

*	flammable liquids (e.g., cleaning supplies, paints, other chemicals)

*	not serviced or not working HVAC equipment

*	unclean air filters

*	makeshift wiring, extension cords longer than 6 feet, electrical cords running under carpets

*	fire and smoke doors left open

*	unattended space heaters

*	construction debris

*	blocked aisles and doorways

Priority Collection Location Maps					Last Updated: 11/06

Comments:

Accurate collection location maps are included in the disaster preparedness plan. The location of priority collections is clearly marked on each map.

Priority items include the following:  Whitman-APD collection AR 2000.002; Rare and Fragile collection; Laws police records P.001; McCallum papers AR E.004; Pease papers AR.001, AR.1998.007, AR.2000.001; cemetery records AR.1994.030, AR.2001.003; Travis county school census; photographs in cabinets; newspaper index card files; Donor file cabinets; O. Henry collection; City directories; Travis county court house drawings; AHC drawings; Austin file negatives; negatives in the photo lab; and one shelf of music videocassettes in the video room. Priority item lists are posted by some priority collections, however, there is yellow tape marking priority item shelves in all of the designated locations.  All disaster preparedness plans contain priority collection location maps.

Electrical Wiring  							Last updated: 11/06

Comments:

Check outlets for excessive plugs.  Look for any exposed wires.  Check lamps, computers, and other electrical equipment.  Be alert to any misuse of appliances (especially hot plates and microwave ovens in the staff room) daily.  Always make sure that equipment is turned off at the end of the day.

***noticed some exposed wiring in the 3rd floor vault area near the phone jack.

****in music video section of basement-all the new video archive system being installed with lots of wires and plugs.  Many items plugged into one power strip.  Should examined.  This equipment has not yet been tested.

At staff desks, there are numerous cords and wires for equipment.  May want to purchase cord holders or come up with some other safe way of dealing with loose cords and wires.

The first, second, and third floors each have a breaker box which is located in the Stacks area of each floor.  They are located on the North wall and these boxes will allow you to disable an individual circuit one at a time.  Each circuit is individually marked.

The Basement/Ground Floor breaker box is located in the basement mechanical room.  The box is on the West wall.  Again, all circuits are individually marked and each box is gray in color.

Fire Alarms and extinguishers				Last updated: 11-2006

Fire alarms and extinguishers should be tested regularly.

All were tested November 2006 by APL security staff. They are on a regular schedule of testing.

Appliances:								Last updated:11-2006

Comments:

All appliances, coffee makers, fans, etc. are unplugged when not in use.  All staff, building security and building custodial personnel are reminded to make certain that all appliances, coffee makers, fans, etc. are unplugged at the end of the day.

Staff microwave oven was replaced in 2006 when old model started causing electrical problems. It was overloading the circuits in the kitchen and causing the circuit breakers to switch off. Ramon Cantu, ACFS, recommended replacement of the microwave – really old models use too much electricity and can cause this type of overload.

Vault sprinkler system:						Last updated: 11-2006

Comments:

The sprinkler in the inner vault needs to be checked annually.  The pipes need to be examined for leaks and the sprinkler heads should be inspected and tested by an inspector.  The latter can be done without releasing water in the vault.  (per Val Musson, message dated 2/13/2003 indicated that the last inspection was 3/24/2002)

Fire Hazards Survey

Last Updated: 11/2006

1.   Have you previously had fire problems in your library?   Yes.

Summer of 2002, strong smell of smoke.  Fire Department investigated and found problem with HVAC fan.

Did any of the problems result in an electrical fire? Yes___ No X

Date of occurrence _______

Were library materials affected?  Yes___ No X   To what extent?

2.   Do you have dependably regular trash collection within your library?  Yes X No___

How often are wastebaskets emptied? checked and emptied daily in the kitchen and restrooms.  staff desk areas a few times a week.  (i think).

Are there areas inside your unit where trash builds up before collection? Yes____ No X

Where?

How much?

3.   Are flammable materials used in your building? Yes X  No___

What kinds?

As the AHC has a black-and-white photography laboratory in its basement, there are chemicals in the building. The photo lab contains the following chemicals:

Kodak Decktol developer

Kodak lens cleaner

Kodak sodium sulfite (anhydrous)

Sepia toner part A

Sepia toner part B

Kodak photo-flo 200

Kodak rapid fixer solution A

Kodak rapid fixer solution B

Kodak indicator stop bath

Kodak rapid selenium toner

Duro Navel jelly

Ilford 2000 RT developer

Ilford 2000 RT fixer

Formula 409 cleaner

Perma Wash solution

Ilford systems cleaner parts AB&C

Kodak developer D-76

Ivory dishwashing liquid

How and where are they stored?  photo lab

How and how often are they disposed of?   used and disposed of in the normal course of business

4.   Do you have a book drop built into an exterior wall? Yes___ No X

Have you ever had flammable materials dropped into it? (If yes, please explain)

Have you had any other type of vandalism of the drop?

Risk Assessment: Water

All areas checked by Tim and Mike on Monday, 11/20/06

Plumbing:

1.	Basement:

a.	Loose tiles under the sink and toilet in the women’s restroom (near elevator)

2.	1st floor:

a.	Signs of old water damage under sink in maintenance closet (next to elevator).

b.	Cut-off valves missing under sink in staff restroom (next to elevator) and the Fire Sprinkler Control Room. Also, paint is bubbling and cracking along walls.

3.	2nd floor:

a.	Staff bathroom: u-joint under sink heavily stained with hard water/mineral deposits.

Ceilings:

·	Basement:

o	Ceiling tiles missing in G5, above window in Oversize Volumes stacks.

o	Water stained and bulging ceiling tiles in G18 (rare/fragile)

o	Discolored tile (possible water) in AMN stacks (tile is along East wall, end of 3rd row of shelves).

o	Paint on ceiling in supplies storage (across from photo lab) is cracked and chipping.

·	1st floor:

o	Cracking pain in the Northwest corner of the Reception Room.

o	Paint peeling around edges of O’Henry room.

·	2nd floor:

o	Stains down the wall in the Archives Workroom (like something dripped down the wall). Same on the facing just above the top of the stairs (between workroom and Ruth’s office). There is also some cracked/bubbling paint in the Southwest corner, extending from the ceiling to halfway down the wall. Ceiling tiles show water stains in the Southeast and Southwest corners.

o	Water stains on ceiling tiles above office door to 203 (Asst. Manager). Also stained and bulging tiles in the Southwest corner of office.

o	Cracked/bubbling paint in Southeast corner of 204 (Cindy’s office).

o	Stained ceiling tiles in Southwest corner of 207 (Irene’s office)

HVAC:

·	2nd Floor:

o	Some staining around vents in 201 (archives). Vents are in the windowsills in the Southwest and Southeast corners.

o	Water stain (relatively new) around AC vent above lion statue in Ruth’s office.

·	Vault:

o	Water stains around HVAC pipes between inner and outer vaults (on both sides of the wall). Also, water stains around pipes leading to roof and pipes leading from blowers to ceiling (inner vault).

o	Green tube (drip tube?) hanging down from electrical outlet in inner vault.

Roof:

·	Roof access door locked – Lt Panacci of AFD (2006) indicated that that is proper and it is not to be an escape route for staff in case of fire.

Doors/Windows:

·	Basement:

o	Some water stains on windowsill in staff break room

o	rust stains on window interior pane of G10 (periodicals)

o	Standing water on windowsill (window is on 9th street side of building) in Oversize Volumes stacks. Also signs of water leaking down into the wall (bubbling paint).

o	Baseboards loose, evidence of rust, and bubbling paint around exterior doorways in the Video Archivist work area. Also beneath fire extinguisher in same area.

o	Water damaged window sills in G2 - Travis County archives (all but western most window). One window is cracked. Paint is peeling above windows. Paint is also peeling along western wall.

·	1st floor:

o	Cracked window in Fire Sprinkler Control room.

o	Caulking cracked around windows in Reception Room, with some minor staining on windowsills.

o	Exterior doors (9th St. and Guadalupe St.) have light coming through and are not seated properly.

o	Peeling paint around North-facing window in Mayor’s Room.

o	Cracked and peeling paint on windowsills in Reading Room.

Risk Assessment Form:  Water

Plumbing							     Last Updated: 11/20/2006

Ceilings							     Last Updated: 11/20/2006

HVAC							                 Last Updated:

Area locked-we have no keys

Roof								     Last Updated: 11/20/2006

Doors and Windows					      	     Last Updated: 11/20/2006

Water Survey

B.	Have there been any recent problems related to the plumbing in your building? Yes _X___   No_____

If yes, explain, giving locations and dates of occurrence:

12/12/2005 – Kitchen faucet leak in basement kitchen.

05/15//2006 – Public men’s room near reading room blocked up.

05/31/2006 – Men’s toilet in the basement blocked up; breakroom and parts of basement hallway flooded with  1-2 in. water.

06/03/2006 – Ice maker in first floor kitchen broken.

06/04/2006 – Problem with refrigerator seal in first floor kitchen reported.

07/03/2006 – Water leak from small a/c vent on balcony of archives room near the top of the stairs reported.

07/29/2006 – Bubbling paint in oversize stack area reported.

08/07/2006 – Strange tubing from electrical outlet to carry condensation in 3rd floor inner vault reported.

09/17/2006 - Mold reported in 3rd floor inner vault reported, installation of door seals requested.

10/17/2006 – Center trim piece on Guadalupe Street entrance door causing poor seal reported.

Flooding in two locations in photo lab(possibly from pipes in wall) reported.

C.	Have you ever experienced leakage around windows, skylights, ceilings, or doors after rain? Yes__X   ___ No____

If yes, explain, giving dates and locations of occurrences:

Signs of leakage found in several window areas during inspection on 11/20/2006. (See Mike’s notes)

D.	Are there water pipes running through collection areas? Yes* _X___ No_____

* HVAC pipes in inner vault on 3rd floor.  There may be other pipes in ceiling that are not visible.

E.	Have you ever experienced leaks attributable to those pipes? Yes _*X_ No_

If yes, explain, giving dates and locations of occurrences and describing any damage to collections resulting from the leaks: Known chiller water carrier over the art rack rails in the Art Rack Room.

Risk Assessment Form:  Security

Intruder Alarm						      Last Updated: 11/2006

The fire and burglary system is tested daily by the alarm monitor company.  If the company does not receive a test signal every day, they contact APL security.  The system also has a state required inspection each year.  The fire alarm is also tested when we have periodic fire drills a few times a year.

Security Radio					                   Last Updated: 11/2006

The security radio is checked daily to be sure that it can send and receive.  Training in using the radios is included in new employee orientation.  Information about security radio use is in the Security Manual next to the cash register at RRI. During a staff meeting in 2006, all staff present that day were shown proper radio usage by security guard.

Reading Room Staff					      Last Updated:  11/2006

An adequate # of staff is in the reading room to monitor researchers and provide reference service?

Current procedures require two employees in the building at all times.  While the reading room has two staff members scheduled, when one has to leave the room to retrieve materials, the other may be in the position of making customers wait or leaving the reading room unattended at times.

General Staff			      			      Last Updated: 11/2006

All telephone reference and general AHC staff is familiar with procedures for responding to bomb threats?

Procedures for responding to a bomb threat are found in the APL Security Manual.  We do not have telephone reference staff at this time. Grace McEvoy will distribute that information to staff in December 2006.

Risk Assessment Form: Interior Risks

Utilities

A walk-through examination of utilities should be performed annually by a utilities specialist, per the Disaster Preparedness Plan.  This was done in December 2006 by ACFS staff member, Floyd Hodges and AHC staff person, Cynthia Lewis.

Housekeeping

No risks are apparent.  Custodial staff seems to keep building as clean as possible, given the fragmented arrangement of the building and its crowded condition.

Trash

Trash is emptied regularly.

Submitted by Kent Middleton and Ruth Baker.

Risk Assessment Form: Exterior Risks

Trees

No tree limbs appear to pose any threat to the building or to vehicles, except possibly the large oak tree at the west end of the building.  It extends slightly over the roof, but given the angle of the limbs, it does not seem to pose a threat.

Hedges and Shrubs

Some plantings around the building slightly touch the building, but don’t pose any problem at present.  However, pruning should be done soon on crepe myrtles to the west of the Ninth Street entrance, at the southeast corner of the building, and at the northeast corner.

Vents and Bird’s Nests

No evidence of birds nesting in vents

Submitted by Kent Middleton and Ruth Baker.

Information Update Form

Emergency Personnel				      Last Updated: 11/22/2006

Comments:

Add new members:

Mike Miller  mike.miller@ci.austin.tx.us

Ben Grillot  ben.grillot@ci.austin.tx.us

Change:

Toni Lambert is now the Assistant Manager of Public Services.

Armando Cubriel is now the Assistant Manager of Building Facilities Services

Ramon Cantu was replaced by Floyd Hodge.

Val Musson’s phone # is 974-7401

Eyna Canalas-Zarate is now listed as Assistant Director.

The AHC Personnel listing in the Disaster Plan needs various changes.  Refer to the AHC personnel telephone tree.

Initials:  SJ & IG

Emergency Equipment and Supplies		      Last Updated:  11/22/2006

Comments:

Basement – no fire pull or fire extinguisher in Periodicals stacks.

Request pending to put fire extinguisher in Mayor’s Room-resolved in 12/2006.

Ruth’s office needs fire extinguisher re-mounted-requested 2/2007.

No first aid kit in RRII desk-requested 2/2007.

First aid kits - Eric’s office is now Mike’s office.

No infection control kit located in staff room kitchen-requested 2/2007.

Add transistor radio in Staff Reference Area, but it needs batteries-order requested 2/2007.

Initials: SJ & IG

Emergency Services				                   Last Updated: 11/22/2006

Comments:

Unable to verify phone # to water main cut-off, but it probably should be 972-1000.

Unable to open any of the breaker boxes, even though there are keys provided-requested 2/2007.

Initials: SJ & IG

Disaster Recovery Supplies – Internal Resources        Last Updated:  11/22/2006

Comments:

Disaster Plan states there are three kits, but only two are described (the location of the third is not known)-changed as of 2/2007.  Neither of the two cans are secured with tape, so there is no guarantee that none of the supplies have been removed.  Also, we will need to replace the old Disaster Plan in each can with a copy of the updated plan.

Initials: SJ & IG

Disaster Recovery Services &Conservation Consultants    Last Updated: 11/22/2006

Comments: It appears to be okay.

Initials:  SJ & IG

Disaster Recovery Procedures			 Last Updated: 11/22/2006

Last Comments:

Procedures for recovery of materials damaged by fire, water, infestation, mold and other growths, theft and vandalism, data loss, chemical spills, bomb threat or tornado should be reviewed to ensure that they agree with current conservation practices.

New Comments:

Recovery Procedures seems consistent with our prevention and emergency procedures.  Do they agree with current conservation practices?  Irene and Scott cannot make that determination, although the Recovery Procedures appear to be fairly up-to-date and reasonable.

Initials: SJ & IG